## Roof Replacement Summary
Location Number | Location | Roof Information | [9 empty] | Visual Condition Assessment | [6 empty] | Condition Summary |  |  | Budget Planning Information
|  | Roof Identification Number | School Number | Level | Area Name | Roof Type | Area (Sq. Ft.) | Roof Type | Date Installed | Deck Information | Age (Years) | Drainage 0-Good Slope/No Ponding 3-Low Slope/Some Ponding 5-Poor Slope/Ponding | Blisters 0-No Blisters 3-Less Than 20 Percent 5-More Than 20 Percent | Linear Folds/Cracks 0-No Folds/Cracks 3-Less Than 20 Percent 5-More Than 20 Percent | Flashing Condition 0-Good 3-Some Splits/Cracks 5-Poor Splits/Cracks Common | Leakage Problems 0-No leaks 3-Minor Leaks 5-Major Leaks | Surface Wear 0-No Wear Noted 3-Average Wear Noted 5-Excessive Wear Noted | Deck 0-Concrete 3-Metal 5-Wood | Total Condition Score | Estimated Service Life | Estimated Remain Life | Estimated Replacement Cost | Recommended Action | Selected Referendum Condition (1) | Recommended Replacement Year | Preliminary Budget
142 | LaFollette | R10 | R10 | 00R | ROOF | ROOF | 13724 | MANVILLE DYNAKAP FR | 1993-08-01 | METAL | 11 | 3 | 3 | 0 | 3 | 5 | 3 | 3 | 46 | 20 | 9 | 82344 | REPLACE | POOR | 1 | 82344
142 | LaFollette | R13 | R13 | 00R | ROOF | ROOF | 7280 | UNKNOWN | 1993-08-01 | METAL | 11 | 3 | 3 | 0 | 3 | 3 | 3 | 3 | 36 | 20 | 9 | 43680 | REPAIR | POOR | 1 | 43680
071 | Lindbergh | R02 | R02 | 00R | ROOF | ROOF | 15558 | SIPLAST PARADIENE 20/30 FR | 1987-08-01 | METAL | 17 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 42 | 20 | 3 | 93348 | REPLACE | POOR | 1 | 137028
071 | Lindbergh | R03 | R03 | 00R | ROOF | ROOF | 3486 | SIPLAST PARADIENE 20/30 FR | 1986-08-01 | METAL | 18 | 3 | 3 | 3 | 3 | 0 | 3 | 0 | 21 | 20 | 2 | 20916 | REPLACE | POOR | 1 | 157944
071 | Lindbergh | R04 | R04 | 00R | ROOF | ROOF | 4474 | SIPLAST PARADIENE 20/30 FR | 1984-08-01 | METAL | 20 | 3 | 3 | 0 | 3 | 0 | 3 | 0 | 15 | 20 | 0 | 26844 | REPAIR | POOR | 1 | 184788
021 | Mendota | R02 | R02 | 00R | ROOF | ROOF | 582 | MANVILLE DYNAKAP FR | 1987-08-01 | CONCRETE | 17 | 5 | 0 | 5 | 3 | 0 | 5 | 0 | 28 | 20 | 3 | 3492 | REPLACE | POOR | 1 | 188280
021 | Mendota | R03 | R03 | 00R | ROOF | ROOF | 4545 | MANVILLE DYNAKAP FR | 1987-08-01 | WOOD | 17 | 5 | 3 | 5 | 3 | 3 | 5 | 5 | 56 | 20 | 3 | 27270 | REPLACE | POOR | 1 | 215550
021 | Mendota | R04 | R04 | 00R | ROOF | ROOF | 9829 | MANVILLE DYNAKAP FR | 1987-08-01 | WOOD | 17 | 3 | 3 | 5 | 3 | 3 | 5 | 5 | 52 | 20 | 3 | 58974 | REPLACE | POOR | 1 | 274524
021 | Mendota | R05 | R05 | 00R | ROOF | ROOF | 6639 | MANVILLE DYNAKAP FR | 1987-08-01 | WOOD | 17 | 5 | 3 | 5 | 3 | 0 | 5 | 0 | 31 | 20 | 3 | 39834 | REPLACE | POOR | 1 | 314358
021 | Mendota | R07 | R07 | 00R | ROOF | ROOF | 1282 | MANVILLE DYNAKAP FR | 1987-08-01 | WOOD | 17 | 5 | 0 | 0 | 3 | 0 | 5 | 0 | 18 | 20 | 3 | 7692 | REPLACE | POOR | 1 | 322050
022 | Midvale | R01 | R01 | 00R | GYM ROOF | ROOF | 7634 | CELOTEX-CELOPAL-I | 1985-08-01 | GYPSUM | 19 | 0 | 3 | 3 | 0 | 0 | 3 | 0 | 12 | 20 | 1 | 45804 | REPAIR | POOR | 1 | 367854
022 | Midvale | R02 | R02 | 00R | ROOF | ROOF | 8593 | SIPLAST PARADIENE 20/30 FR | 1981-08-01 | UNKNOWN | 23 | 3 | 5 | 3 | 3 | 0 | 3 | 0 | 23 | 20 | -3 | 51558 | REPLACE | POOR | 1 | 419412
022 | Midvale | R03 | R03 | 00R | ROOF | ROOF | 9763 | CELOTEX CP101C | 1986-08-01 | UNKNOWN | 18 | 5 | 5 | 3 | 3 | 2 | 5 | 5 | 49 | 20 | 2 | 58578 | REPLACE | POOR | 1 | 477990
143 | West | R05 | R05 | 00R | ROOF | ROOF | 988 | SIPLAST PARADIENE 20/30 FR | 1986-08-01 | METAL | 18 | 5 | 0 | 0 | 5 | 3 | 3 | 3 | 39 | 20 | 2 | 5928 | REPLACE | POOR | 1 | 483918
143 | West | R20 | R20 | 00R | ROOF | ROOF | 1273 | BUR 4-PLY | 1965-08-01 | UNKNOWN | 39 | 5 | 0 | 0 | 5 | 3 | 3 | 5 | 43 | 20 | -19 | 7638 | REPLACE | POOR | 1 | 491556
227 | Whitehorse | R13 | R13 | 00R | ROOF | ROOF | 14315 | TAMKO VERSA CAP FR 2-PLY | 1995-08-01 | METAL | 9 | 3 | 5 | 3 | 3 | 3 | 3 | 3 | 44 | 20 | 11 | 85890 | REPLACE | POOR | 1 | 577446
227 | Whitehorse | R14 | R14 | 00R | ROOF | ROOF | 13183 | UNKNOWN | 1989-08-01 | METAL | 15 | 3 | 5 | 0 | 0 | 3 | 3 | 3 | 35 | 20 | 5 | 79098 | REPLACE | POOR | 1 | 656544
210 | Blackhawk | R17 | R17 | 00R | RELOCATABLE NORTH | ROOF | 1053 | UNKNOWN | 1965-08-01 | UNKNOWN | 39 | 0 | 0 | 0 | 5 | 3 | 3 | 5 | 33 | 20 | -19 | 6318 | REPLACE | POOR | 2 | 6318
210 | Blackhawk | R18 | R18 | 00R | RELOCATABLE EAST | ROOF | 1227 | UNKNOWN | 1965-08-01 | UNKNOWN | 39 | 0 | 0 | 0 | 5 | 3 | 3 | 5 | 33 | 20 | -19 | 7362 | REPLACE | POOR | 2 | 13680
141 | East | P01 | P01 | 00R | PLAZA | PLAZA - LOCKER RM AREA | 9776 | CONCRETE/MEMBRANE | 1970-08-01 | CONCRETE | 34 | 5 | 0 | 0 | 3 | 5 | 3 | 0 | 41 | 35 | 1 | 293280 | REPLACE | POOR | 2 | 306960
141 | East | P02 | P02 | 00R | PLAZA | PLAZA - COOLING TOWER ARE | 829 | CONCRETE PAVERS/MEMBRANE | 1970-08-01 | CONCRETE | 34 | 5 | 0 | 0 | 3 | 0 | 0 | 0 | 13 | 35 | 1 | 24870 | REPAIR | POOR | 2 | 331830
220 | O'Keeffe | R04 | R04 | 00R | ROOF | ROOF | 3445 | EPDM BALLAST | 1986-08-01 | WOOD | 18 | 0 | 0 | 0 | 3 | 3 | 3 | 5 | 31 | 15 | -3 | 20670 | REPLACE | POOR | 2 | 352500
228 | Sherman | C01 | C01 | 00R | CANOPY | CANOPY | 122 | COAL TAR | 1960-08-01 | WOOD | 44 | 0 | 5 | 0 | 3 | 0 | 5 | 0 | 13 | 20 | -24 | 732 | REPLACE | POOR | 2 | 353232
228 | Sherman | C02 | C02 | 00R | CANOPY | CANOPY | 128 | COAL TAR | 1960-08-01 | WOOD | 44 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 8 | 20 | -24 | 768 | REPAIR | POOR | 2 | 354000
228 | Sherman | R01 | R01 | 00R | ROOF | ROOF | 9931 | TEMPORARY ROOF | 1996-08-01 | METAL | 8 | 0 | 5 | 1 | 3 | 0 | 3 | 0 | 13 | 7 | -1 | 59586 | REPAIR | POOR | 2 | 413586
228 | Sherman | R04 | R04 | 00R | ROOF | ROOF | 7434 | FIRESTONE-(MECH-FASTENED) | 1994-08-01 | WOOD | 10 | 3 | 0 | 0 | 0 | 3 | 0 | 5 | 31 | 15 | 5 | 44604 | REPLACE | POOR | 2 | 458190
029 | Shorewood | R02 | R02 | 00R | ROOF | ROOF | 3672 | 3-PLY TEMP | 1996-08-01 | METAL | 8 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 7 | -1 | 22032 | REPAIR | POOR | 2 | 480222
029 | Shorewood | R03 | R03 | 00R | ROOF | ROOF | 3017 | 3-PLY TEMP | 1996-08-01 | METAL | 8 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 7 | -1 | 18102 | REPAIR | POOR | 2 | 498324
029 | Shorewood | R07 | R07 | 00R | ROOF | ROOF | 3664 | GRACE GRM-500 | 1984-08-01 | TAMKO 15# FELT, 2.2" ISOC | 20 | 3 | 3 | 0 | 3 | 3 | 3 | 5 | 40 | 7 | -13 | 21984 | REPLACE | POOR | 2 | 520308
029 | Shorewood | R08 | R08 | 00R | ROOF | ROOF | 8664 | MODIFIED BIT. | 1990-08-01 | METAL | 14 | 3 | 3 | 3 | 0 | 3 | 3 | 3 | 39 | 15 | 1 | 51984 | REPLACE | POOR | 2 | 572292
225 | Toki | R07 | R07 | 00R | ROOF | ROOF | 5165 | TARMAC SBS FR | 1992-08-01 | METAL | 12 | 5 | 3 | 3 | 3 | 5 | 3 | 3 | 56 | 20 | 8 | 30990 | REPLACE | POOR | 2 | 603282
225 | Toki | R09 | R09 | 00R | ROOF | ROOF | 5042 | MANVILLE DYNAKAP FR | 1989-08-01 | METAL | 15 | 3 | 3 | 0 | 3 | 0 | 3 | 0 | 15 | 20 | 5 | 30252 | REPAIR | POOR | 2 | 633534
225 | Toki | R10 | R10 | 00R | ROOF | ROOF | 3279 | MANVILLE DYNAKAP FR | 1989-08-01 | METAL | 15 | 3 | 3 | 3 | 3 | 0 | 3 | 0 | 21 | 20 | 5 | 19674 | REPAIR | POOR | 2 | 653208
225 | Toki | R11 | R11 | 00R | ROOF | ROOF | 4935 | MANVILLE DYNAKAP FR | 1989-08-01 | METAL | 15 | 5 | 5 | 3 | 3 | 0 | 3 | 0 | 27 | 20 | 5 | 29610 | REPLACE | POOR | 2 | 682818
225 | Toki | R16 | R16 | 00R | ROOF | RELOCATABLE ROOF | 1611 | ASPHALT ROLLED ROOFING | 1962-08-01 | WOOD | 42 | 5 | 0 | 0 | 5 | 3 | 3 | 5 | 43 | 20 | -22 | 9666 | REPLACE | POOR | 2 | 692484
225 | Toki | R18 | R18 | 00R | ROOF | ROOF | 12545 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | METAL | 2 | 3 | 5 | 3 | 3 | 0 | 0 | 0 | 20 | 5 | 3 | 75270 | REPLACE | POOR | 2 | 767754
001 | Allis | R02 | R02 | 00R | GYM | ROOF | 6031 | SIPLAST PARADIENE 20/30 FR | 1985-08-01 | UNKNOWN | 19 | 3 | 1 | 0 | 0 | 0 | 3 | 0 | 10 | 20 | 1 | 36186 | REPAIR | POOR | 3 | 36186
001 | Allis | R04 | R04 | 00R | ROOF | ROOF | 2899 | SIPLAST PARADIENE 20/30 FR | 1985-08-01 | UNKNOWN | 19 | 3 | 0 | 0 | 1 | 3 | 3 | 5 | 35 | 20 | 1 | 17394 | REPLACE | POOR | 3 | 53580
001 | Allis | R05 | R05 | 00R | ROOF | ROOF | 2010 | SIPLAST PARADIENE 20/30 FR | 1985-08-01 | UNKNOWN | 19 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | 1 | 12060 | REPAIR | POOR | 3 | 65640
001 | Allis | R06 | R06 | 00R | ROOF | ROOF | 4510 | SIPLAST PARADIENE 20/30 FR | 1985-08-01 | UNKNOWN | 19 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | 1 | 27060 | REPAIR | POOR | 3 | 92700
001 | Allis | R07 | R07 | 00R | ROOF | ROOF | 5973 | SIPLAST PARADIENE 20/30 FR | 1985-08-01 | UNKNOWN | 19 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | 1 | 35838 | REPAIR | POOR | 3 | 128538
001 | Allis | R08 | R08 | 00R | ROOF | ROOF | 3602 | SIPLAST PARADIENE 20/30 FR | 1985-08-01 | UNKNOWN | 19 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | 1 | 21612 | REPAIR | POOR | 3 | 150150
001 | Allis | R09 | R09 | 00R | ROOF | ROOF | 7390 | SIPLAST PARADIENE 20/30 FR | 1985-08-01 | UNKNOWN | 19 | 3 | 3 | 0 | 0 | 0 | 3 | 0 | 12 | 20 | 1 | 44340 | REPAIR | POOR | 3 | 194490
001 | Allis | R11 | R11 | 00R | ENTRANCE | ROOF | 335 | COPPER | 1965-08-01 | UNKNOWN | 39 | 0 | 0 | 0 | 5 | 3 | 3 | 5 | 33 | 15 | -24 | 2010 | REPLACE | POOR | 3 | 196500
203 | Cherokee | R01 | R01 | 00R | ROOF | ROOF | 15998 | EPDM BALLAST | 1984-08-01 | METAL | 20 | 3 | 0 | 0 | 0 | 3 | 3 | 3 | 30 | 15 | -5 | 95988 | REPLACE | POOR | 3 | 292488
203 | Cherokee | R02 | R02 | 00R | ROOF | ROOF | 11017 | EPDM BALLAST | 1984-08-01 | METAL | 20 | 3 | 0 | 0 | 0 | 3 | 3 | 3 | 30 | 15 | -5 | 66102 | REPLACE | POOR | 3 | 358590
004 | Crestwood | R04 | R04 | 00R | GYM | ROOF | 4735 | ARC | 1988-08-01 | METAL | 16 | 0 | 0 | 0 | 5 | 0 | 3 | 0 | 8 | 20 | 4 | 28410 | REPLACE | POOR | 3 | 387000
004 | Crestwood | R06 | R06 | 00R | ENTRANCE | ROOF | 724 | ARC | 1988-08-01 | METAL | 16 | 5 | 3 | 0 | 3 | 0 | 3 | 0 | 19 | 20 | 4 | 4344 | REPAIR | POOR | 3 | 391344
004 | Crestwood | R08 | R08 | 00R | ROOF | ROOF | 4600 | DERBIGUM-HPS | 1982-08-01 | METAL | 22 | 5 | 3 | 3 | 3 | 0 | 3 | 0 | 25 | 20 | -2 | 27600 | REPLACE | POOR | 3 | 418944
004 | Crestwood | R11 | R11 | 00R | LMC | ROOF | 2688 | GAF RUBEROID MB 131 MGPFR | 1993-06-03 | METAL | 11 | 3 | 5 | 3 | 3 | 3 | 3 | 3 | 44 | 20 | 9 | 16128 | REPLACE | POOR | 3 | 435072
004 | Crestwood | R14 | R14 | 00R | LMC | ROOF | 121 | GAF RUBEROID MB 131 MGPFR | 1993-06-03 | METAL | 11 | 3 | 3 | 0 | 5 | 0 | 5 | 0 | 19 | 20 | 9 | 726 | REPLACE | POOR | 3 | 435798
004 | Crestwood | R15 | R15 | 00R | LMC | ROOF | 485 | GAF RUBEROID MB 131 MGPFR | 1993-06-03 | METAL | 11 | 5 | 5 | 0 | 3 | 3 | 5 | 3 | 44 | 20 | 9 | 2910 | REPLACE | POOR | 3 | 438708
141 | East | R13 | R13 | 00R | ROOF | ROOF | 1926 | GRACE GRM 500 | 1986-08-01 | METAL | 18 | 3 | 0 | 0 | 3 | 5 | 3 | 3 | 43 | 15 | -3 | 11556 | REPLACE | POOR | 3 | 450264
141 | East | R17 | R17 | 00R | ROOF | ROOF | 6579 | MANVILLE DYNAKAP FR, EXIS | 1987-08-01 | METAL | 17 | 5 | 3 | 3 | 3 | 0 | 3 | 0 | 25 | 20 | 3 | 39474 | REPLACE | POOR | 3 | 489738
141 | East | R27 | R27 | 00R | ROOF | ROOF | 1539 | CARLISLE SURE-SEAL EPDM 4 | 1981-08-01 | CONCRETE | 23 | 0 | 0 | 0 | 5 | 0 | 3 | 0 | 8 | 15 | -8 | 9234 | REPLACE | POOR | 3 | 498972
141 | East | R28 | R28 | 00R | ROOF | ROOF | 320 | CARLISLE SURE-SEAL EPDM 4 | 1981-08-01 | CONCRETE | 23 | 0 | 0 | 0 | 5 | 0 | 3 | 0 | 8 | 15 | -8 | 1920 | REPLACE | POOR | 3 | 500892
141 | East | R32 | R32 | 00R | ROOF | ROOF | 1171 | MODIFIED BIT. | 1981-08-01 | METAL | 23 | 0 | 5 | 0 | 5 | 0 | 5 | 0 | 15 | 20 | -3 | 7026 | REPLACE | POOR | 3 | 507918
141 | East | R33 | R33 | 00R | ROOF | ROOF | 3836 | MANVILLE DYNAKAP FR, ISO/ | 1987-08-01 | METAL | 17 | 0 | 5 | 0 | 5 | 0 | 0 | 0 | 10 | 20 | 3 | 23016 | REPLACE | POOR | 3 | 530934
008 | Franklin | R01 | R01 | 00R | ROOF | ROOF | 2133 | UNKNOWN | 1965-08-01 | UNKNOWN | 39 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | -19 | 12798 | REPAIR | POOR | 3 | 543732
008 | Franklin | R02 | R02 | 00R | ROOF | ROOF | 3019 | GEOFLEX-PIB | 1982-08-01 | WOOD | 22 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -2 | 18114 | REPAIR | POOR | 3 | 561846
008 | Franklin | R03 | R03 | 00R | ROOF | ROOF | 3033 | UNKNOWN | 1965-08-01 | UNKNOWN | 39 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -19 | 18198 | REPAIR | POOR | 3 | 580044
008 | Franklin | R06 | R06 | 00R | ROOF | ROOF | 2340 | SIPLAST PARADIENE 20/30 FR | 1985-08-01 | METAL | 19 | 0 | 0 | 0 | 3 | 3 | 3 | 3 | 27 | 20 | 1 | 14040 | REPLACE | POOR | 3 | 594084
008 | Franklin | R09 | R09 | 00R | ROOF | ROOF | 225 | UNKNOWN | 1965-08-01 | UNKNOWN | 39 | 3 | 0 | 0 | 3 | 3 | 3 | 5 | 37 | 20 | -19 | 1350 | REPLACE | POOR | 3 | 595434
234 | Hamilton | R17 | R17 | 00R | ROOF | ROOF | 7366 | SIPLAST PARADIENE 20/30 FR | 1988-08-01 | METAL | 16 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 9 | 20 | 4 | 44196 | REPAIR | POOR | 3 | 639630
234 | Hamilton | R18 | R18 | 00R | ROOF | ROOF | 2780 | SIPLAST PARADIENE 20/30 FR | 1988-08-01 | METAL | 16 | 3 | 3 | 0 | 0 | 3 | 3 | 3 | 33 | 20 | 4 | 16680 | REPLACE | POOR | 3 | 656310
234 | Hamilton | R19 | R19 | 00R | ROOF | ROOF | 2812 | SIPLAST PARADIENE 20/30 FR | 1988-08-01 | METAL | 16 | 3 | 3 | 0 | 0 | 0 | 3 | 0 | 12 | 20 | 4 | 16872 | REPAIR | POOR | 3 | 673182
234 | Hamilton | R24 | R24 | 00R | ROOF | ROOF | 1228 | BUR 4-PLY | 1962-08-01 | WOOD | 42 | 3 | 0 | 0 | 3 | 3 | 5 | 5 | 39 | 20 | -22 | 7368 | REPLACE | POOR | 3 | 680550
009 | Glendale | R01 | R01 | 00R | R00F | ROOF | 13675 | FIRESTONE EPDM W/BALLAST | 1989-08-01 | METAL | 15 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 15 | 0 | 82050 | REPAIR | POOR | 4 | 82050
009 | Glendale | R06 | R06 | 00R | R00F | ROOF | 11236 | FIRESTONE EPDM W/BALLAST | 1989-08-01 | METAL | 15 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 15 | 0 | 67416 | REPAIR | POOR | 4 | 149466
009 | Glendale | R07 | R07 | 00R | R00F | ROOF | 11389 | FIRESTONE EPDM W/BALLAST | 1989-08-01 | METAL | 15 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 15 | 0 | 68334 | REPAIR | POOR | 4 | 217800
245 | Jefferson | R01 | R01 | 00R | ROOF | ROOF | 12411 | SIPLAST PARADIENE 20/30 FR | 1989-08-01 | METAL | 15 | 3 | 3 | 0 | 0 | 0 | 3 | 0 | 12 | 20 | 5 | 74466 | REPAIR | POOR | 4 | 292266
245 | Jefferson | R02 | R02 | 00R | ROOF | ROOF | 16841 | SIPLAST PARADIENE 20/30 FR | 1989-08-01 | METAL | 15 | 3 | 5 | 0 | 0 | 3 | 3 | 3 | 35 | 20 | 5 | 101046 | REPLACE | POOR | 4 | 393312
245 | Jefferson | R03 | R03 | 00R | ROOF | ROOF | 10511 | SIPLAST PARADIENE 20/30 FR | 1989-08-01 | METAL | 15 | 3 | 3 | 0 | 0 | 0 | 3 | 0 | 12 | 20 | 5 | 63066 | REPAIR | POOR | 4 | 456378
245 | Jefferson | R04 | R04 | 00R | ROOF | ROOF | 1849 | SIPLAST PARADIENE 20/30 FR | 1989-08-01 | METAL | 15 | 3 | 3 | 0 | 0 | 0 | 3 | 0 | 12 | 20 | 5 | 11094 | REPAIR | POOR | 4 | 467472
245 | Jefferson | R05 | R05 | 00R | ROOF | ROOF | 6698 | SIPLAST PARADIENE 20/30 FR | 1989-08-01 | METAL | 15 | 3 | 5 | 0 | 0 | 3 | 3 | 3 | 35 | 20 | 5 | 40188 | REPLACE | POOR | 4 | 507660
245 | Jefferson | R06 | R06 | 00R | ROOF | ROOF | 1876 | SIPLAST PARADIENE 20/30 FR | 1989-08-01 | METAL | 15 | 3 | 3 | 0 | 0 | 0 | 3 | 0 | 12 | 20 | 5 | 11256 | REPAIR | POOR | 4 | 518916
016 | Lapham | R02 | R02 | 00R | ROOF | ROOF | 7213 | SIPLAST PARADIENE 20/30 FR | 1984-08-01 | CONCRETE | 20 | 3 | 3 | 0 | 3 | 0 | 5 | 0 | 17 | 20 | 0 | 43278 | REPLACE | POOR | 4 | 562194
072 | Leopold | R01 | R01 | 00R | ROOF | ROOF | 3853 | SIPLAST PARADIENE 20/30 FR | 1986-08-01 | METAL | 18 | 0 | 5 | 3 | 0 | 0 | 3 | 0 | 14 | 20 | 2 | 23118 | REPAIR | POOR | 4 | 585312
145 | Memorial | R01 | R01 | 00R | ROOF | GARAGE ROOF | 1450 | EPDM BALLAST | 1988-08-01 | METAL | 16 | 3 | 3 | 3 | 3 | 0 | 5 | 0 | 23 | 15 | -1 | 8700 | REPLACE | POOR | 4 | 594012
145 | Memorial | R02 | R02 | 00R | ROOF | RECEIVING ROOF | 419 | EPDM BALLAST | 1988-08-01 | METAL | 16 | 3 | 3 | 3 | 3 | 0 | 5 | 0 | 23 | 15 | -1 | 2514 | REPLACE | POOR | 4 | 596526
145 | Memorial | R03 | R03 | 00R | ROOF | BOILER ROOM ROOF | 2356 | BUR 4-PLY | 1965-08-01 | METAL | 39 | 0 | 3 | 3 | 3 | 0 | 5 | 0 | 17 | 20 | -19 | 14136 | REPLACE | POOR | 4 | 610662
023 | Thoreau | R01 | R01 | 00R | ROOF | ROOF | 4752 | SIPLAST PARADIENE 20/30 FR | 1985-08-01 | 2.2" ISOCYANURATE, (2) LA | 19 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | 1 | 28512 | REPAIR | POOR | 4 | 639174
023 | Thoreau | R02 | R02 | 00R | ROOF | ROOF | 2622 | SIPLAST PARADIENE 20/30 FR | 1985-08-01 | 2.2" ISOCYANURATE, (2) LA | 19 | 0 | 3 | 0 | 3 | 0 | 5 | 0 | 11 | 20 | 1 | 15732 | REPLACE | POOR | 4 | 654906
023 | Thoreau | R07 | R07 | 00R | ROOF | ROOF | 5516 | SIPLAST PARADIENE 20/30 FR | 1985-08-01 | 2.2" ISOCYANURATE, (2) LA | 19 | 0 | 3 | 3 | 0 | 0 | 3 | 0 | 12 | 20 | 1 | 33096 | REPAIR | POOR | 4 | 688002
023 | Thoreau | R08 | R08 | 00R | ROOF | ROOF | 5196 | FIRESTONE EPDM W/BALLAST | 1992-08-01 | METAL | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 3 | 31176 | MAINTAIN | POOR | 4 | 719178
023 | Thoreau | R09 | R09 | 00R | ROOF | ROOF | 1766 | FIRESTONE EPDM W/BALLAST | 1992-08-01 | METAL | 12 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 15 | 3 | 10596 | REPAIR | POOR | 4 | 729774
023 | Thoreau | R10 | R10 | 00R | ROOF | ROOF | 2204 | SIPLAST PARADIENE 20/30 FR | 1992-08-01 | METAL | 12 | 0 | 3 | 0 | 3 | 0 | 5 | 0 | 11 | 15 | 3 | 13224 | REPLACE | POOR | 4 | 742998
037 | Lincoln | R01 | R01 | 00R | ROOF | ROOF | 7818 | CELOTEX-CELOPAL-I | 1986-08-01 | METAL | 18 | 0 | 5 | 0 | 0 | 0 | 3 | 0 | 8 | 20 | 2 | 46908 | REPAIR | POOR | 5 | 46908
037 | Lincoln | R02 | R02 | 00R | ROOF | ROOF | 6245 | CELOTEX-CELOPAL-I | 1986-08-01 | METAL | 18 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | 2 | 37470 | REPAIR | POOR | 5 | 84378
037 | Lincoln | R03 | R03 | 00R | ROOF | ROOF | 6397 | CELOTEX-CELOPAL-I | 1986-08-01 | METAL | 18 | 1 | 3 | 0 | 0 | 0 | 3 | 0 | 8 | 20 | 2 | 38382 | REPAIR | POOR | 5 | 122760
037 | Lincoln | R04 | R04 | 00R | ROOF | ROOF | 3004 | CELOTEX-CELOPAL-I | 1986-08-01 | METAL | 18 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | 2 | 18024 | REPAIR | POOR | 5 | 140784
037 | Lincoln | R06 | R06 | 00R | ROOF | ROOF | 5272 | CELOTEX-CELOPAL-I | 1986-08-01 | METAL | 18 | 0 | 3 | 1 | 3 | 0 | 3 | 0 | 11 | 20 | 2 | 31632 | REPAIR | POOR | 5 | 172416
037 | Lincoln | R07 | R07 | 00R | ROOF | ROOF | 4941 | CELOTEX-CELOPAL-I | 1986-08-01 | METAL | 18 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | 2 | 29646 | REPAIR | POOR | 5 | 202062
037 | Lincoln | R08 | R08 | 00R | ROOF | ROOF | 6951 | CELOTEX-CELOPAL-I | 1986-08-01 | METAL | 18 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | 2 | 41706 | REPAIR | POOR | 5 | 243768
037 | Lincoln | R09 | R09 | 00R | ROOF | ROOF | 5728 | CELOTEX-CELOPAL-I | 1986-08-01 | METAL | 18 | 0 | 3 | 2 | 2 | 0 | 3 | 0 | 12 | 20 | 2 | 34368 | REPAIR | POOR | 5 | 278136
037 | Lincoln | R10 | R10 | 00R | ROOF | ROOF | 4047 | CELOTEX-CELOPAL-I | 1986-08-01 | METAL | 18 | 0 | 2 | 0 | 0 | 0 | 4 | 0 | 6 | 20 | 2 | 24282 | REPAIR | POOR | 5 | 302418
037 | Lincoln | R11 | R11 | 00R | ROOF | ROOF | 11011 | CELOTEX-CELOPAL-I | 1986-08-01 | METAL | 18 | 0 | 1 | 0 | 0 | 0 | 4 | 0 | 5 | 20 | 2 | 66066 | REPAIR | POOR | 5 | 368484
242 | Sennett | C01 | C01 | 00R | Main Entrance Canopy | Canopy | 153 | MANVILLE DYNAKAP FR,2.2" | 1989-08-01 | STEEL/CONCRETE | 15 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | 5 | 918 | REPAIR | POOR | 5 | 369402
242 | Sennett | C02 | C02 | 00R | Rear Entrance | Canopy | 158 | MANVILLE DYNAKAP FR,2.2" | 1989-08-01 | STEEL/CONCRETE | 15 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | 5 | 948 | REPAIR | POOR | 5 | 370350
242 | Sennett | R01 | R01 | 00R | Old Cafeteria | ROOF | 875 | BUR 4-PLY | 1980-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -4 | 5250 | REPAIR | POOR | 5 | 375600
242 | Sennett | R02 | R02 | 00R | GYM NW AREA | ROOF | 1575 | MANVILLE DYNAKAP FR,2.2" | 1989-08-01 | STEEL/CONCRETE | 15 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 6 | 20 | 5 | 9450 | REPAIR | POOR | 5 | 385050
242 | Sennett | R03 | R03 | 00R | GYM ROOF SW | ROOF | 1573 | MANVILLE DYNAKAP FR,2.2" | 1989-08-01 | STEEL/CONCRETE | 15 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | 5 | 9438 | REPAIR | POOR | 5 | 394488
242 | Sennett | R04 | R04 | 00R | GYM ROOF NE | ROOF | 1584 | MANVILLE DYNAKAP FR, 2.2" | 1989-08-01 | STEEL/CONCRETE | 15 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | 5 | 9504 | REPAIR | POOR | 5 | 403992
242 | Sennett | R05 | R05 | 00R | GYM ROOF SE | ROOF | 1583 | MANVILLE DYNAKAP FR,2.2" | 1989-08-01 | STEEL/CONCRETE | 15 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | 5 | 9498 | REPAIR | POOR | 5 | 413490
242 | Sennett | R06 | R06 | 00R | UPPER MECH NORTH | ROOF | 1413 | MANVILLE DYNAKAP FR,2.2" | 1989-08-01 | STEEL/CONCRETE | 15 | 3 | 3 | 0 | 3 | 0 | 3 | 0 | 15 | 20 | 5 | 8478 | REPAIR | POOR | 5 | 421968
242 | Sennett | R07 | R07 | 00R | UPPER MECH SOUTH | ROOF | 1406 | MANVILLE DYNAKAP FR,2.2" | 1989-08-01 | STEEL/CONCRETE | 15 | 3 | 3 | 3 | 3 | 0 | 3 | 0 | 21 | 20 | 5 | 8436 | REPAIR | POOR | 5 | 430404
242 | Sennett | R08 | R08 | 00R | CLASSROOM NW | ROOF | 2763 | MANVILLE DYNAKAP FR,2.2" | 1989-08-01 | STEEL/CONCRETE | 15 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | 5 | 16578 | REPAIR | POOR | 5 | 446982
242 | Sennett | R09 | R09 | 00R | ROOF | ROOF | 2293 | MANVILLE DYNAKAP FR,2.2" | 1989-08-01 | STEEL/CONCRETE | 15 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | 5 | 13758 | REPAIR | POOR | 5 | 460740
242 | Sennett | R10 | R10 | 00R | ROOF | ROOF | 2744 | MANVILLE DYNAKAP FR, 2.2" | 1989-08-01 | STEEL/CONCRETE | 15 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | 5 | 16464 | REPAIR | POOR | 5 | 477204
242 | Sennett | R11 | R11 | 00R | ROOF | ROOF | 2634 | MANVILLE DYNAKAP FR,2.2" | 1989-08-01 | STEEL/CONCRETE | 15 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 6 | 20 | 5 | 15804 | REPAIR | POOR | 5 | 493008
242 | Sennett | R12 | R12 | 00R | ROOF | ROOF | 2210 | MANVILLE DYNAKAP FR,2.2" | 1989-08-01 | STEEL/CONCRETE | 15 | 3 | 3 | 0 | 3 | 0 | 3 | 0 | 15 | 20 | 5 | 13260 | REPAIR | POOR | 5 | 506268
242 | Sennett | R13 | R13 | 00R | ROOF | ROOF | 2617 | MANVILLE DYNAKAP FR,2.2" | 1989-08-01 | STEEL/CONCRETE | 15 | 3 | 3 | 0 | 3 | 0 | 3 | 0 | 15 | 20 | 5 | 15702 | REPAIR | POOR | 5 | 521970
242 | Sennett | R14 | R14 | 00R | ROOF | ROOF | 2713 | MANVILLE DYNAKAP FR, 2.2" | 1989-08-01 | STEEL/CONCRETE | 15 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | 5 | 16278 | REPAIR | POOR | 5 | 538248
242 | Sennett | R15 | R15 | 00R | ROOF | ROOF | 2243 | MANVILLE DYNAKAP FR, 2.2" | 1989-08-01 | STEEL/CONCRETE | 15 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 6 | 20 | 5 | 13458 | REPAIR | POOR | 5 | 551706
242 | Sennett | R16 | R16 | 00R | ROOF | ROOF | 2691 | MANVILLE DYNAKAP FR,2.2" | 1989-08-01 | STEEL/CONCRETE | 15 | 0 | 5 | 0 | 3 | 0 | 3 | 0 | 11 | 20 | 5 | 16146 | REPAIR | POOR | 5 | 567852
242 | Sennett | R17 | R17 | 00R | ROOF | ROOF | 2708 | MANVILLE DYNAKAP FR,2.2" | 1989-08-01 | STEEL/CONCRETE | 15 | 0 | 3 | 0 | 3 | 3 | 3 | 3 | 30 | 20 | 5 | 16248 | REPLACE | POOR | 5 | 584100
242 | Sennett | R18 | R18 | 00R | ROOF | ROOF | 2250 | MANVILLE DYNAKAP FR, 2.2" | 1989-08-01 | STEEL/CONCRETE | 15 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 6 | 20 | 5 | 13500 | REPAIR | POOR | 5 | 597600
242 | Sennett | R19 | R19 | 00R | ROOF | ROOF | 2676 | MANVILLE DYNAKAP FR,2.2" | 1989-08-01 | STEEL/CONCRETE | 15 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | 5 | 16056 | REPAIR | POOR | 5 | 613656
242 | Sennett | R20 | R20 | 00R | ROOF | ROOF | 1276 | MANVILLE DYNAKAP FR, 2.2" | 1989-08-01 | STEEL/CONCRETE | 15 | 3 | 3 | 0 | 3 | 0 | 3 | 0 | 15 | 20 | 5 | 7656 | REPAIR | POOR | 5 | 621312
143 | West | R04 | R04 | 00R | ROOF | ROOF | 9737 | SIPLAST PARADIENE 20/30 FR | 1986-08-01 | METAL | 18 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | 2 | 58422 | REPAIR | POOR | 5 | 679734
143 | West | R06 | R06 | 00R | ROOF | ROOF | 2521 | SIPLAST PARADIENE 20/30 FR | 2000-08-01 | METAL | 4 | 5 | 5 | 0 | 0 | 0 | 3 | 0 | 18 | 15 | 11 | 15126 | REPAIR | POOR | 5 | 694860
143 | West | R07 | R07 | 00R | ROOF | ROOF | 5712 | SIPLAST PARADIENE 20/30 FR | 1986-08-01 | METAL | 18 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | 2 | 34272 | REPAIR | POOR | 5 | 729132
143 | West | R08 | R08 | 00R | ROOF | ROOF | 706 | SIPLAST PARADIENE 20/30 FR | 1986-08-01 | METAL | 18 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | 2 | 4236 | REPAIR | POOR | 5 | 733368
Total Area Scheduled for Replacement: | [6 empty] | 568173 | [9 empty] | Preliminary Budget Estimate: |  |  |  |  | 3663558
(1) Red indicates manual selection.