## Background
Background
The Madison Metropolitan School District roof inventory consists of over 2.9 million square feet of roofing area. Individual school worksheets supply roofing data to the "Roof Summary" worksheet. Changes to data are made by individual locations. Information regarding roof type, deck type and year installed was collected from previous roofing replacement work or existing building data. Roof area and roof identification number is cross referenced from existing AutoCad drawings for each facility. Visual inspection of roof sections were conducted by Building Services staff within the last 6 months. Data catagories include exsting drainage/slope conditions; extent of blisters (trapped moisture); extent of linear folds/cracks; flashing condition; leakage problems based on work orders history; and surface wear. Service life is based on industry standards for expected life of various systems and ranges from 15 years for a Single Membrane EPDM rubber type roofing system to 75 years for a Clay Tile system.
Condition Score
Condition Score is a calculated weighted formula based on visual data inputs with weight given to conditions that contribute to premature system failure (Drainage Condition and Linear Folds/Cracks) and conditions that indicate system failure (Leakage). Deck contributes to the total condition score only if Leakage is indicated, as wet deck conditions of metal decking contributes to deck failure due to rust, and wet deck conditions of wood decking contributes to deck failure due to wood rot and mold.
Estimated Remaining Life
Estimated remaining life is calculated using the installed date (age in years) subtracted from the Estimated Service Life based on the "Roof Type" indicated.
Recommended/Selected Action
Recommended action is calculated using logical selection criterial that looks at Estimated Remaining Life, Total Condition Score and Visual data inputs to recommend if a roof section is to be "Maintained" (indicating good condition), Repaired (Indicating increased maintenance is expected to extend service life and minimize failures), or "Replace" (Indicating system is at or beyond its expected service life and Visual inspection data indicates signs of system failure). Based on the Recommended action analysis, each selection is reviewed to determine the selected action based on physical layout of facility, condition of other roof sections within the facility and estimated remaining life. This selection is then used to develope the Roofing Replacement Schedule that prioritizes roofing to be considered for the next 5 year maintenance plan based on total dollars need to maintain a 20 to 25 year roofing replacement schedule.
| Median Economic System Life Spans (years): |  |  | Unit Price | Units
| Roofing: | Aluminum Frame/Glass | 50 | 65 | sf
|  | Built - Up | 20 | 5.4 | sf
|  | Clay Tile | 75 | 15 | sf
|  | Concrete Tile | 50 | 15 | sf
|  | EPDM | 15 | 4 | sf
|  | Shingle | 15 | 2 | sf
|  | Steel | 25 | 5.4 | sf
|  | Unknown | 15 | 5.4 | sf
|  | Temporary | 7 | 5.4 | sf

## Roof Summary
Location Number | Location | Roof Information | [9 empty] | Visual Condition Assessment | [6 empty] | Condition Summary |  |  | Budget Planning Information
|  | Roof Identification Number | School Number | Level | Area Name | Roof Type | Area (Sq. Ft.) | Roof Type | Date Installed | Deck Information | Age (Years) | Drainage 0-Good Slope/No Ponding 3-Low Slope/Some Ponding 5-Poor Slope/Ponding | Blisters 0-No Blisters 3-Less Than 20 Percent 5-More Than 20 Percent | Linear Folds/Cracks 0-No Folds/Cracks 3-Less Than 20 Percent 5-More Than 20 Percent | Flashing Condition 0-Good 3-Some Splits/Cracks 5-Poor Splits/Cracks Common | Leakage Problems 0-No leaks 3-Minor Leaks 5-Major Leaks | Surface Wear 0-No Wear Noted 3-Average Wear Noted 5-Excessive Wear Noted | Deck 0-Concrete 3-Metal 5-Wood | Total Conditon Score | Estimated Service Life | Estimated Remain Life | Estimated Replacement Cost | Recommended Action | Selected Referendum Condition (1)
301 | Administration | C01 | C01 | 00R | CANOPY | CANOPY | 162 | UNKNOWN | 1995-08-01 | UNKNOWN | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | -16 | 900 | MAINTAIN | GOOD
301 | Administration | C02 | C02 | 00R | CANOPY | CANOPY | 18 | UNKNOWN | 1995-08-01 | UNKNOWN | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | -16 | 100 | MAINTAIN | GOOD
301 | Administration | R01 | R01 | 00R | ROOF | ROOF | 3796 | MANVILLE DYNAGLAS FR | 1994-08-01 | CONCRETE | 32 | 3 | 3 | 0 | 2 | 0 | 3 | 0 | 14 | 20 | -12 | 20500 | REPAIR | FAIR
301 | Administration | R02 | R02 | 00R | ROOF | ROOF | 68 | MANVILLE DYNAGLAS FR | 1994-08-01 | CONCRETE | 32 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -12 | 400 | REPAIR | FAIR
301 | Administration | R03 | R03 | 00R | ROOF | ROOF | 6985 | MANVILLE DYNAGLAS FR | 1994-08-01 | CONCRETE | 32 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -12 | 37700 | REPAIR | FAIR
301 | Administration | R04 | R04 | 00R | ROOF | ROOF | 3314 | MANVILLE DYNAGLAS FR | 1994-08-01 | CONCRETE | 32 | 0 | 3 | 0 | 5 | 3 | 3 | 0 | 26 | 20 | -12 | 17900 | REPLACE | POOR
301 | Administration | R05 | R05 | 00R | ROOF | ROOF | 526 | MANVILLE DYNAGLAS FR | 1994-08-01 | CONCRETE | 32 | 3 | 3 | 0 | 5 | 0 | 3 | 0 | 17 | 20 | -12 | 2800 | REPLACE | POOR
301 | Administration | R06 | R06 | 00R | ROOF | ROOF | 5679 | MANVILLE DYNAGLAS FR | 1994-08-01 | CONCRETE | 32 | 0 | 5 | 5 | 5 | 0 | 3 | 0 | 23 | 20 | -12 | 30700 | REPLACE | POOR
301 | Administration | R07 | R07 | 00R | ROOF | ROOF | 603 | MANVILLE DYNAGLAS FR | 1994-08-01 | CONCRETE | 32 | 3 | 3 | 0 | 0 | 0 | 0 | 0 | 9 | 20 | -12 | 3300 | REPAIR | FAIR
301 | Administration | R08 | R08 | 00R | ROOF | ROOF | 4194 | MANVILLE DYNAGLAS FR | 1994-08-01 | CONCRETE | 32 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -12 | 22600 | REPAIR | FAIR
301 | Administration | R09 | R09 | 00R | ROOF | ROOF | 2418 | MANVILLE DYNAGLAS FR | 1994-08-01 | CONCRETE | 32 | 3 | 3 | 0 | 3 | 0 | 3 | 0 | 15 | 20 | -12 | 13100 | REPLACE | POOR
301 | Administration | R10 | R10 | 00R | ROOF | ROOF | 392 | MANVILLE DYNAGLAS FR | 1994-08-01 | CONCRETE | 32 | 3 | 5 | 0 | 3 | 0 | 3 | 0 | 17 | 20 | -12 | 2100 | REPAIR | FAIR
301 | Administration | R11 | R11 | 00R | ROOF | ROOF | 171 | MANVILLE DYNAGLAS FR | 1994-08-01 | CONCRETE | 32 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -12 | 900 | REPAIR | FAIR
301 | Administration | R12 | R12 | 00R | ROOF | ROOF | 5436 | MANVILLE DYNAGLAS FR | 1994-08-01 | CONCRETE | 32 | 3 | 0 | 0 | 3 | 0 | 3 | 0 | 12 | 20 | -12 | 29400 | REPLACE | POOR
301 | Administration | R13 | R13 | 00R | ROOF | ROOF | 3369 | MANVILLE DYNAGLAS FR | 1994-08-01 | CONCRETE | 32 | 0 | 5 | 5 | 3 | 0 | 3 | 0 | 21 | 20 | -12 | 18200 | REPLACE | POOR
301 | Administration | R14 | R14 | 00R | ROOF | ROOF | 3196 | MANVILLE DYNAGLAS FR | 1994-08-01 | CONCRETE | 32 | 5 | 3 | 0 | 3 | 0 | 3 | 0 | 19 | 20 | -12 | 17300 | REPAIR | FAIR
001 | Allis | C01 | C01 | 00R | CANOPY | ROOF | 97 | SIPLAST PARADIENE 20/30 FR | 2004-08-04 | UNKNOWN | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | -7 | 500 | MAINTAIN | GOOD
001 | Allis | C02 | C02 | 00R | CANOPY | ROOF | 97 | SIPLAST PARADIENE 20/30 FR | 2004-08-04 | UNKNOWN | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | -7 | 500 | MAINTAIN | GOOD
001 | Allis | C03 | C03 | 00R | CANOPY | ROOF | 64 | SIPLAST PARADIENE 20/30 FR | 2004-08-04 | UNKNOWN | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | -7 | 300 | MAINTAIN | GOOD
001 | Allis | C04 | C04 | 00R | CANOPY | ROOF | 142 | SIPLAST PARADIENE 20/30 FR | 2004-08-04 | UNKNOWN | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | -7 | 800 | MAINTAIN | GOOD
001 | Allis | R01 | R01 | 00R | LOCKER | ROOF | 2551 | SIPLAST PARADIENE 20/30 FR | 2004-08-04 | UNKNOWN | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | -7 | 13800 | MAINTAIN | GOOD
001 | Allis | R02 | R02 | 00R | GYM | ROOF | 6031 | SIPLAST PARADIENE 20/30 FR | 1985-08-01 | UNKNOWN | 41 | 3 | 1 | 0 | 0 | 0 | 3 | 0 | 10 | 20 | -21 | 32600 | REPAIR | POOR
001 | Allis | R03 | R03 | 00R | TRACTOR | ROOF | 309 | SIPLAST PARADIENE 20/30 FR | 2004-08-04 | UNKNOWN | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -2 | 1700 | MAINTAIN | GOOD
001 | Allis | R04 | R04 | 00R | ROOF | ROOF | 2899 | SIPLAST PARADIENE 20/30 FR | 1985-08-01 | UNKNOWN | 41 | 3 | 0 | 0 | 1 | 3 | 3 | 5 | 35 | 20 | -21 | 15700 | REPLACE | POOR
001 | Allis | R05 | R05 | 00R | ROOF | ROOF | 2010 | SIPLAST PARADIENE 20/30 FR | 1985-08-01 | UNKNOWN | 41 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -21 | 10900 | REPAIR | POOR
001 | Allis | R06 | R06 | 00R | ROOF | ROOF | 4510 | SIPLAST PARADIENE 20/30 FR | 1985-08-01 | UNKNOWN | 41 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -21 | 24400 | REPAIR | POOR
001 | Allis | R07 | R07 | 00R | ROOF | ROOF | 5973 | SIPLAST PARADIENE 20/30 FR | 1985-08-01 | UNKNOWN | 41 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -21 | 32300 | REPAIR | POOR
001 | Allis | R08 | R08 | 00R | ROOF | ROOF | 3602 | SIPLAST PARADIENE 20/30 FR | 1985-08-01 | UNKNOWN | 41 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -21 | 19500 | REPAIR | POOR
001 | Allis | R09 | R09 | 00R | ROOF | ROOF | 7390 | SIPLAST PARADIENE 20/30 FR | 1985-08-01 | UNKNOWN | 41 | 3 | 3 | 0 | 0 | 0 | 3 | 0 | 12 | 20 | -21 | 39900 | REPAIR | POOR
001 | Allis | R10 | R10 | 00R | ROOF | ROOF | 954 | SIPLAST PARADIENE 20/30 FR | 2004-08-04 | UNKNOWN | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | -7 | 5200 | MAINTAIN | GOOD
001 | Allis | R11 | R11 | 00R | ENTRANCE | ROOF | 335 | COPPER | 1965-08-01 | UNKNOWN | 61 | 0 | 0 | 0 | 5 | 3 | 3 | 5 | 33 | 15 | -46 | 1800 | REPLACE | POOR
210 | Blackhawk | PH01 | PH01 | 00R | PENTHOUSE | ROOF | 1269 | BUR 4-PLY | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4 | 6900 | MAINTAIN | GOOD
210 | Blackhawk | PH02 | PH02 | 00R | PENTHOUSE | ROOF | 2256 | BUR 4-PLY | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4 | 12200 | MAINTAIN | GOOD
210 | Blackhawk | R01 | R01 | 00R | ROOF | ROOF | 3313 | BUR 4-PLY | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4 | 17900 | MAINTAIN | GOOD
210 | Blackhawk | R02 | R02 | 00R | ROOF | ROOF | 5198 | BUR 4-PLY | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4 | 28100 | MAINTAIN | GOOD
210 | Blackhawk | R03 | R03 | 00R | ROOF | ROOF | 2298 | BUR 4-PLY | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4 | 12400 | MAINTAIN | GOOD
210 | Blackhawk | R04 | R04 | 00R | ROOF | ROOF | 7673 | BUR 4-PLY | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4 | 41400 | MAINTAIN | GOOD
210 | Blackhawk | R05 | R05 | 00R | ROOF | ROOF | 10807 | BUR 4-PLY | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4 | 58400 | MAINTAIN | GOOD
210 | Blackhawk | R07 | R07 | 00R | ROOF | ROOF | 7227 | BUR 4-PLY | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4 | 39000 | MAINTAIN | GOOD
210 | Blackhawk | R08 | R08 | 00R | ROOF | ROOF | 8498 | BUR 4-PLY | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4 | 45900 | MAINTAIN | GOOD
210 | Blackhawk | R09 | R09 | 00R | ROOF | ROOF | 5734 | SIPLAST PARADIENE 20/30 FR | 1990-08-01 | METAL | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -16 | 31000 | MAINTAIN | GOOD
210 | Blackhawk | R10 | R10 | 00R | ROOF | ROOF | 11284 | BUR 4-PLY | 2002-08-01 | UNKNOWN | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4 | 60900 | MAINTAIN | GOOD
210 | Blackhawk | R11 | R11 | 00R | ROOF | ROOF | 8371 | BUR 4-PLY | 2002-08-01 | UNKNOWN | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4 | 45200 | MAINTAIN | GOOD
210 | Blackhawk | R12 | R12 | 00R | ROOF | ROOF | 1740 | DERBIGUM HPS, COMP INS (2 | 1983-08-01 | METAL | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -23 | 9400 | MAINTAIN | GOOD
210 | Blackhawk | R13 | R13 | 00R | ROOF | ROOF | 2960 | SIPLAST PARADIENE 20/30 FR | 2003-08-01 | CONCRETE | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -3 | 16000 | MAINTAIN | GOOD
210 | Blackhawk | R14 | R14 | 00R | ROOF | ROOF | 419 | SIPLAST PARADIENE 20/30 FR | 2003-08-01 | METAL | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -3 | 2300 | MAINTAIN | GOOD
210 | Blackhawk | R15 | R15 | 00R | ROOF | ROOF | 8538 | GAF GAFGLAS 4-PLY W/GRAV | 1991-08-01 | WOOD | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -15 | 46100 | MAINTAIN | GOOD
210 | Blackhawk | R16 | R16 | 00R | ROOF | ROOF | 30712 | GAF GAFGLAS 4-PLY W/GRAV | 1991-08-01 | WOOD | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -15 | 165800 | MAINTAIN | GOOD
210 | Blackhawk | R17 | R17 | 00R | RELOCATABLE NORTH | ROOF | 1053 | UNKNOWN | 1965-08-01 | UNKNOWN | 61 | 0 | 0 | 0 | 5 | 3 | 3 | 5 | 33 | 15 | -46 | 5700 | REPLACE | POOR
210 | Blackhawk | R18 | R18 | 00R | RELOCATABLE EAST | ROOF | 1227 | UNKNOWN | 1965-08-01 | UNKNOWN | 61 | 0 | 0 | 0 | 5 | 3 | 3 | 5 | 33 | 15 | -46 | 6600 | REPLACE | POOR
052 | Chavez | R01 | R01 | 00R | GYM | ROOF | 9895 | SIPLAST PARADIENE 20/30 FR | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5 | 53400 | MAINTAIN | GOOD
052 | Chavez | R02 | R02 | 00R | CANOPY | ROOF | 52 | SIPLAST PARADIENE 20/30 FR | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5 | 300 | MAINTAIN | GOOD
052 | Chavez | R03 | R03 | 00R | ADMINISTRATIVE | ROOF | 5915 | SIPLAST PARADIENE 20/30 FR | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5 | 31900 | MAINTAIN | GOOD
052 | Chavez | R04 | R04 | 00R | ROOF | ROOF | 1056 | SIPLAST PARADIENE 20/30 FR | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5 | 5700 | MAINTAIN | GOOD
052 | Chavez | R05 | R05 | 00R | THIRD-GRADE | ROOF | 6543 | SIPLAST PARADIENE 20/30 FR | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5 | 35300 | MAINTAIN | GOOD
052 | Chavez | R06 | R06 | 00R | CAFE-LMC | ROOF | 7709 | SIPLAST PARADIENE 20/30 FR | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5 | 41600 | MAINTAIN | GOOD
052 | Chavez | R07 | R07 | 00R | MECHANICAL | ROOF | 1778 | SIPLAST PARADIENE 20/30 FR | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5 | 9600 | MAINTAIN | GOOD
052 | Chavez | R08 | R08 | 00R | ROOF | ROOF | 2908 | SIPLAST PARADIENE 20/30 FR | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5 | 15700 | MAINTAIN | GOOD
052 | Chavez | R09 | R09 | 00R | CANOPY | ROOF | 226 | SIPLAST PARADIENE 20/30 FR | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5 | 1200 | MAINTAIN | GOOD
052 | Chavez | R10 | R10 | 00R | FOURTH-GRADE | ROOF | 9366 | SIPLAST PARADIENE 20/30 FR | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5 | 50600 | MAINTAIN | GOOD
052 | Chavez | R11 | R11 | 00R | KINDERGARTEN | ROOF | 609 | SIPLAST PARADIENE 20/30 FR | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5 | 3300 | MAINTAIN | GOOD
052 | Chavez | R12 | R12 | 00R | CANOPY | ROOF | 226 | SIPLAST PARADIENE 20/30 FR | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5 | 1200 | MAINTAIN | GOOD
052 | Chavez | R13 | R13 | 00R | FIFTH-GRADE | ROOF | 6367 | SIPLAST PARADIENE 20/30 FR | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5 | 34400 | MAINTAIN | GOOD
052 | Chavez | R14 | R14 | 00R | ROOF | ROOF | 1043 | SIPLAST PARADIENE 20/30 FR | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5 | 5600 | MAINTAIN | GOOD
052 | Chavez | R15 | R15 | 00R | RECEIVING | ROOF | 3384 | SIPLAST PARADIENE 20/30 FR | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5 | 18300 | MAINTAIN | GOOD
203 | Cherokee | R01 | R01 | 00R | ROOF | ROOF | 15998 | EPDM BALLAST | 1984-08-01 | METAL | 42 | 3 | 0 | 0 | 0 | 3 | 3 | 3 | 30 | 15 | -27 | 64000 | REPLACE | POOR
203 | Cherokee | R02 | R02 | 00R | ROOF | ROOF | 11017 | EPDM BALLAST | 1984-08-01 | METAL | 42 | 3 | 0 | 0 | 0 | 3 | 3 | 3 | 30 | 15 | -27 | 44100 | REPLACE | POOR
203 | Cherokee | R03 | R03 | 00R | ROOF | ROOF | 18103 | SIPLAST PARADIENE 20/30 FR TG | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5 | 97800 | MAINTAIN | GOOD
203 | Cherokee | R04 | R04 | 00R | ROOF | ROOF | 281 | SIPLAST PARADIENE 20/30 FR TG | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5 | 1500 | MAINTAIN | GOOD
203 | Cherokee | R05 | R05 | 00R | ROOF | ROOF | 910 | SIPLAST PARADIENE 20/30 FR TG | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5 | 4900 | MAINTAIN | GOOD
203 | Cherokee | R06 | R06 | 00R | ROOF | ROOF | 4056 | SIPLAST PARADIENE 20/30 FR TG | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5 | 21900 | MAINTAIN | GOOD
203 | Cherokee | R07 | R07 | 00R | ROOF | ROOF | 327 | SIPLAST PARADIENE 20/30 FR TG | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5 | 1800 | MAINTAIN | GOOD
004 | Crestwood | R01 | R01 | 00R | GYM | ROOF | 3654 | GAF RUBEROID MB 131 MGPFR | 1993-06-03 | ACOUSTICAL-METAL | 33 | 0 | 5 | 3 | 3 | 0 | 3 | 0 | 17 | 20 | -13 | 19700 | REPAIR | FAIR
004 | Crestwood | R02 | R02 | 00R | KITCHEN | ROOF | 507 | SIPLAST PARADIENE 20/30 FR | 2003-08-01 | METAL | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -3 | 2700 | MAINTAIN | GOOD
004 | Crestwood | R03 | R03 | 00R | KITCHEN | ROOF | 702 | SIPLAST PARADIENE 20/30 FR | 2003-08-01 | METAL | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -3 | 3800 | MAINTAIN | GOOD
004 | Crestwood | R04 | R04 | 00R | GYM | ROOF | 4735 | ARC | 1988-08-01 | METAL | 38 | 0 | 0 | 0 | 5 | 0 | 3 | 0 | 8 | 20 | -18 | 25600 | REPLACE | POOR
004 | Crestwood | R05 | R05 | 00R | LOCKER | ROOF | 1981 | SIPLAST PARADIENE 20/30 FR | 2003-08-01 | METAL | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -3 | 10700 | MAINTAIN | GOOD
004 | Crestwood | R06 | R06 | 00R | ENTRANCE | ROOF | 724 | ARC | 1988-08-01 | METAL | 38 | 5 | 3 | 0 | 3 | 0 | 3 | 0 | 19 | 20 | -18 | 3900 | REPAIR | POOR
004 | Crestwood | R07 | R07 | 00R | ROOF | ROOF | 8715 | SIPLAST PARADIENE 20/30 FR | 2003-08-01 | WOOD | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -3 | 47100 | MAINTAIN | GOOD
004 | Crestwood | R08 | R08 | 00R | ROOF | ROOF | 4600 | DERBIGUM-HPS | 1982-08-01 | METAL | 44 | 5 | 3 | 3 | 3 | 0 | 3 | 0 | 25 | 20 | -24 | 24800 | REPLACE | POOR
004 | Crestwood | R09 | R09 | 00R | ELEVATOR | ROOF | 540 | GAF RUBEROID MB 131 MGPFR | 1993-06-03 | METAL | 33 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | -13 | 2900 | REPAIR | FAIR
004 | Crestwood | R10 | R10 | 00R | ROOF | ROOF | 7106 | BUR 4-PLY | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4 | 38400 | MAINTAIN | GOOD
004 | Crestwood | R11 | R11 | 00R | LMC | ROOF | 2688 | GAF RUBEROID MB 131 MGPFR | 1993-06-03 | METAL | 33 | 3 | 5 | 3 | 3 | 3 | 3 | 3 | 44 | 20 | -13 | 14500 | REPLACE | POOR
004 | Crestwood | R12 | R12 | 00R | LMC | ROOF | 2980 | GAF RUBEROID MB 131 MGPFR | 1993-06-03 | METAL | 33 | 3 | 5 | 3 | 3 | 0 | 3 | 0 | 23 | 20 | -13 | 16100 | REPLACE | POOR
004 | Crestwood | R13 | R13 | 00R | BARREL-LMC | ROOF | 2688 | GAF RUBEROID MB 131 MGPFR | 1993-06-03 | WOOD | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -13 | 14500 | MAINTAIN | GOOD
004 | Crestwood | R14 | R14 | 00R | LMC | ROOF | 121 | GAF RUBEROID MB 131 MGPFR | 1993-06-03 | METAL | 33 | 3 | 3 | 0 | 5 | 0 | 5 | 0 | 19 | 20 | -13 | 700 | REPLACE | POOR
004 | Crestwood | R15 | R15 | 00R | LMC | ROOF | 485 | GAF RUBEROID MB 131 MGPFR | 1993-06-03 | METAL | 33 | 5 | 5 | 0 | 3 | 3 | 5 | 3 | 44 | 20 | -13 | 2600 | REPLACE | POOR
141 | East | GRH1 | GRH1 | 00R | GREEN HOUSE | ROOF | 398 | ALUMINUM FRAME/GLASS | 1987-08-01 | NONE | 39 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 15 | 50 | 11 | 25900 | REPAIR | FAIR
141 | East | GRH2 | GRH2 | 00R | GREEN HOUSE | ROOF | 398 | ALUMINUM FRAME/GLASS | 1995-08-01 | NONE | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 19 | 25900 | MAINTAIN | GOOD
141 | East | P01 | P01 | 00R | PLAZA | PLAZA - LOCKER RM AREA | 9776 | CONCRETE/MEMBRANE | 1970-08-01 | CONCRETE | 56 | 5 | 0 | 0 | 3 | 5 | 3 | 0 | 41 | 35 | -21 | 293280 | REPLACE | POOR
141 | East | P02 | P02 | 00R | PLAZA | PLAZA - COOLING TOWER ARE | 829 | CONCRETE PAVERS/MEMBRANE | 1970-08-01 | CONCRETE | 56 | 5 | 0 | 0 | 3 | 0 | 0 | 0 | 13 | 35 | -21 | 24870 | REPAIR | POOR
141 | East | PH1 | PH1 | 00R | ROOF | PENTHOUSE ROOF | 1228 | SIPLAST PARADIENE 20/30 FR | 1965-08-01 | UNKNOWN | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -41 | 6600 | MAINTAIN | GOOD
141 | East | PH2 | PH2 | 00R | ROOF | PENTHOUSE ROOF | 984 | MODIFIED BIT. | 1965-08-01 | UNKNOWN | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -41 | 5300 | MAINTAIN | GOOD
141 | East | PH3 | PH3 | 00R | ROOF | PENTHOUSE ROOF | 830 | SCHULLER 2FID MODIFIED | 1996-08-01 | METAL | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -10 | 4500 | MAINTAIN | GOOD
141 | East | PH4 | PH4 | 00R | ROOF | PENTHOUSE ROOF | 830 | SCHULLER 2FID MODIFIED | 1996-08-01 | METAL | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -10 | 4500 | MAINTAIN | GOOD
141 | East | PH5 | PH5 | 00R | ROOF | PENTHOUSE ROOF | 863 | SIPLAST PARADIENE 20/30 FR | 2000-08-01 | METAL | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -6 | 4700 | MAINTAIN | GOOD
141 | East | PH6 | PH6 | 00R | ROOF | PENTHOUSE ROOF | 863 | SIPLAST PARADIENE 20/30 FR | 2000-08-01 | METAL | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -6 | 4700 | MAINTAIN | GOOD
141 | East | PH7 | PH7 | 00R | ROOF | PENTHOUSE ROOF | 219 | SIPLAST PARADIENE 20/30 FR | 2000-08-01 | METAL | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -6 | 1200 | MAINTAIN | GOOD
141 | East | R01 | R01 | 00R | ROOF | FIELD HOUSE ROOF | 25931 | MANVILLE GLASPLY-IV 4-PLY | 1991-08-01 | METAL | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -15 | 140000 | MAINTAIN | GOOD
141 | East | R02 | R02 | 00R | ROOF | ROOF | 299 | MANVILLE GLASPLY-IV 4-PLY | 1991-08-01 | METAL | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -15 | 1600 | MAINTAIN | GOOD
141 | East | R04 | R04 | 00R | ROOF | ROOF | 222 | MANVILLE GLASPLY-IV 4-PLY | 1991-08-01 | METAL | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -15 | 1200 | MAINTAIN | GOOD
141 | East | R05 | R05 | 00R | ROOF | ROOF | 23216 | SIPLAST PARADIENE 20/30 FR | 2000-08-01 | CONCRETE | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -6 | 125400 | MAINTAIN | GOOD
141 | East | R06 | R06 | 00R | ROOF | ROOF | 3937 | MANVILLE DYNAGLAS FR | 1995-08-01 | METAL | 31 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 6 | 20 | -11 | 21300 | REPAIR | FAIR
141 | East | R07 | R07 | 00R | ROOF | ROOF | 5372 | MANVILLE DYNAGLAS FR | 1995-08-01 | METAL | 31 | 0 | 3 | 0 | 3 | 3 | 3 | 3 | 30 | 20 | -11 | 29000 | REPLACE | POOR
141 | East | R08 | R08 | 00R | ROOF | ROOF | 2323 | SCHULLER 3FID MODIFIED | 1995-08-01 | METAL | 31 | 0 | 5 | 0 | 3 | 0 | 3 | 0 | 11 | 20 | -11 | 12500 | REPAIR | FAIR
141 | East | R09 | R09 | 00R | ROOF | ROOF | 477 | SCHULLER 3FID MODIFIED | 1995-08-01 | METAL | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -11 | 2600 | MAINTAIN | GOOD
141 | East | R10 | R10 | 00R | ROOF | ROOF | 1832 | SCHULLER 3FID MODIFIED | 1995-08-01 | METAL | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -11 | 9900 | MAINTAIN | GOOD
141 | East | R11 | R11 | 00R | ROOF | ROOF | 478 | SCHULLER 3FID MODIFIED | 1995-08-01 | METAL | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -11 | 2600 | MAINTAIN | GOOD
141 | East | R13 | R13 | 00R | ROOF | ROOF | 1926 | GRACE GRM 500 | 1986-08-01 | METAL | 40 | 3 | 0 | 0 | 3 | 5 | 3 | 3 | 43 | 15 | -25 | 10400 | REPLACE | POOR
141 | East | R14 | R14 | 00R | ROOF | ROOF | 4804 | BUR 4-PLY | 1965-08-01 | UNKNOWN | 61 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 20 | -41 | 25900 | REPAIR | FAIR
141 | East | R15 | R15 | 00R | ROOF | ROOF | 317 | SCHULLER 3FID MODIFIED | 1995-08-01 | METAL | 31 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 6 | 20 | -11 | 1700 | REPAIR | FAIR
141 | East | R16 | R16 | 00R | ROOF | ROOF | 612 | SCHULLER 3FID MODIFIED | 1995-08-01 | METAL | 31 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | -11 | 3300 | REPAIR | FAIR
141 | East | R17 | R17 | 00R | ROOF | ROOF | 6579 | MANVILLE DYNAKAP FR, EXIS | 1987-08-01 | METAL | 39 | 5 | 3 | 3 | 3 | 0 | 3 | 0 | 25 | 20 | -19 | 35500 | REPLACE | POOR
141 | East | R17A | R17A | 00R | ROOF | ROOF | 359 | UNKNOWN | 1965-08-01 | UNKNOWN | 61 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 5 | 20 | -41 | 1900 | REPAIR | FAIR
141 | East | R18 | R18 | 00R | ROOF | ROOF | 2840 | SCHULLER 3FID MODIFIED | 1995-08-01 | METAL | 31 | 0 | 0 | 3 | 3 | 0 | 3 | 0 | 12 | 20 | -11 | 15300 | REPLACE | POOR
141 | East | R18A | R18A | 00R | ROOF | ROOF | 361 | UNKNOWN | 1965-08-01 | UNKNOWN | 61 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 20 | -41 | 1900 | REPAIR | FAIR
141 | East | R19 | R19 | 00R | ROOF | ROOF | 909 | SCHULLER 3FID MODIFIED | 1995-09-01 | METAL | 31 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 8 | 20 | -11 | 4900 | REPAIR | FAIR
141 | East | R20 | R20 | 00R | ROOF | ROOF | 1646 | SCHULLER 3FID MODIFIED | 1995-08-01 | METAL | 31 | 0 | 3 | 3 | 3 | 0 | 3 | 0 | 15 | 20 | -11 | 8900 | REPLACE | POOR
141 | East | R21 | R21 | 00R | ROOF | ROOF | 1121 | SCHULLER 3FID MODIFIED | 1995-08-01 | METAL | 31 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | -11 | 6100 | REPAIR | FAIR
141 | East | R22 | R22 | 00R | ROOF | ROOF | 1774 | SCHULLER 3FID MODIFIED | 1995-08-01 | METAL | 31 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | -11 | 9600 | REPAIR | FAIR
141 | East | R23 | R23 | 00R | ROOF | ROOF | 12321 | SCHULLER 2FID MODIFIED | 1996-08-01 | CONCRETE | 30 | 3 | 3 | 0 | 3 | 0 | 3 | 0 | 15 | 20 | -10 | 66500 | REPAIR | FAIR
141 | East | R24 | R24 | 00R | ROOF | ROOF | 11571 | GRACE GRM 500 | 1965-08-01 | METAL | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -41 | 62500 | MAINTAIN | GOOD
141 | East | R25 | R25 | 00R | ROOF | ROOF | 1325 | SCHULLER 3FID MODIFIED | 1995-08-01 | METAL | 31 | 0 | 5 | 0 | 3 | 0 | 3 | 0 | 11 | 20 | -11 | 7200 | REPAIR | FAIR
141 | East | R25A | R25A | 00R | ROOF | ROOF | 480 | SCHULLER 3FID MODIFIED | 1995-08-01 | METAL | 31 | 0 | 5 | 0 | 3 | 0 | 3 | 0 | 11 | 20 | -11 | 2600 | REPAIR | FAIR
141 | East | R25B | R25B | 00R | ROOF | ROOF | 273 | SCHULLER 3FID MODIFIED | 1995-08-01 | METAL | 31 | 0 | 5 | 0 | 3 | 0 | 3 | 0 | 11 | 20 | -11 | 1500 | REPAIR | FAIR
141 | East | R26 | R26 | 00R | ROOF | ROOF | 307 | CARLISLE SURE-SEAL EPDM 4 | 1981-08-01 | CONCRETE | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | -30 | 1200 | MAINTAIN | GOOD
141 | East | R27 | R27 | 00R | ROOF | ROOF | 1539 | CARLISLE SURE-SEAL EPDM 4 | 1981-08-01 | CONCRETE | 45 | 0 | 0 | 0 | 5 | 0 | 3 | 0 | 8 | 15 | -30 | 6200 | REPLACE | POOR
141 | East | R28 | R28 | 00R | ROOF | ROOF | 320 | CARLISLE SURE-SEAL EPDM 4 | 1981-08-01 | CONCRETE | 45 | 0 | 0 | 0 | 5 | 0 | 3 | 0 | 8 | 15 | -30 | 1300 | REPLACE | POOR
141 | East | R29 | R29 | 00R | ROOF | ROOF | 1668 | MANVILLE DYNAKAP FR, ISO/ | 1987-08-01 | METAL | 39 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 6 | 20 | -19 | 9000 | REPAIR | FAIR
141 | East | R30 | R30 | 00R | ROOF | ROOF | 1735 | MANVILLE DYNAKAP FR, ISO/ | 1987-08-01 | METAL | 39 | 0 | 5 | 0 | 3 | 0 | 3 | 0 | 11 | 20 | -19 | 9400 | REPAIR | FAIR
141 | East | R31 | R31 | 00R | ROOF | ROOF | 8077 | ARMCO 24GA ALUMINIZED STE | 1981-08-01 | METAL | 45 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 3 | 25 | -20 | 43600 | REPAIR | FAIR
141 | East | R32 | R32 | 00R | ROOF | ROOF | 1171 | MODIFIED BIT. | 1981-08-01 | METAL | 45 | 0 | 5 | 0 | 5 | 0 | 5 | 0 | 15 | 20 | -25 | 6300 | REPLACE | POOR
141 | East | R33 | R33 | 00R | ROOF | ROOF | 3836 | MANVILLE DYNAKAP FR, ISO/ | 1987-08-01 | METAL | 39 | 0 | 5 | 0 | 5 | 0 | 0 | 0 | 10 | 20 | -19 | 20700 | REPLACE | POOR
141 | East | R34 | R34 | 00R | ROOF | ROOF | 2862 | MANVILLE DYNAKAP FR, ISO/ | 1987-08-01 | CONCRETE | 39 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | -19 | 15500 | REPAIR | FAIR
141 | East | R35 | R35 | 00R | ROOF | ROOF | 3302 | MANVILLE DYNAKAP FR, ISO/ | 1987-08-01 | CONCRETE | 39 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -19 | 17800 | REPAIR | FAIR
141 | East | R36 | R36 | 00R | ROOF | ROOF | 987 | MANVILLE DYNAKAP FR, ISO/ | 1987-08-01 | CONCRETE | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -19 | 5300 | MAINTAIN | GOOD
141 | East | R37 | R37 | 00R | ROOF | ROOF | 7846 | SCHULLER 2FID MODIFIED | 1996-08-01 | METAL | 30 | 3 | 3 | 0 | 3 | 0 | 3 | 0 | 15 | 20 | -10 | 42400 | REPAIR | FAIR | 1
141 | East | R38 | R38 | 00R | TOWER | ROOF | 529 | SCHULLER 2FID MODIFIED | 1996-08-01 | CONCRETE | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -10 | 2900 | MAINTAIN | GOOD
141 | East | R39 | R39 | 00R | ROOF | ROOF | 12265 | MANVILLE DYNAKAP FR, ISO/ | 1987-08-01 | PRECAST CONCRETE | 39 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 20 | -19 | 66200 | REPAIR | FAIR
141 | East | R40 | R40 | 00R | ROOF | ROOF | 14333 | MANVILLE DYNAKAP FR, ISO/ | 1987-08-01 | CONCRETE | 39 | 0 | 5 | 0 | 3 | 0 | 3 | 0 | 11 | 20 | -19 | 77400 | REPAIR | FAIR
141 | East | R41 | R41 | 00R | ROOF | ROOF | 1190 | MANVILLE DYNAKAP FR, ISO/ | 1987-08-01 | CONCRETE | 39 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | -19 | 6400 | REPAIR | FAIR
141 | East | R42 | R42 | 00R | ROOF | ROOF | 5595 | MANVILLE DYNAKAP FR, ISO/ | 1987-08-01 | PRECAST CONCRETE | 39 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | -19 | 30200 | REPAIR | FAIR
141 | East | R5A | R5A | 00R | ROOF | ROOF | 172 | SIPLAST PARADIENE 20/30 FR | 2000-08-01 | CONCRETE | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -6 | 900 | MAINTAIN | GOOD
141 | East | R5B | R5B | 00R | ROOF | ROOF | 172 | SIPLAST PARADIENE 20/30 FR | 2000-08-01 | CONCRETE | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -6 | 900 | MAINTAIN | GOOD
006 | Elvejhem | R01 | R01 | 00R | ROOF | ROOF | 13630 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | WOOD | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4 | 73600 | MAINTAIN | GOOD
006 | Elvejhem | R02 | R02 | 00R | CAFETERIA | ROOF | 4348 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | WOOD | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4 | 23500 | MAINTAIN | GOOD
006 | Elvejhem | R03 | R03 | 00R | ROOF | ROOF | 26444 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | WOOD | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4 | 142800 | MAINTAIN | GOOD
006 | Elvejhem | R04 | R04 | 00R | ROOF | ROOF | 10552 | GAF GAFGLAS 104G | 1993-12-31 | WOOD | 33 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 6 | 20 | -13 | 57000 | REPAIR | FAIR
006 | Elvejhem | R05 | R05 | 00R | GYM | ROOF | 5418 | GAF GAFGLAS 104G | 1993-12-31 | ACOUSTICAL-METAL | 33 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -13 | 29300 | REPAIR | FAIR
006 | Elvejhem | R06 | R06 | 00R | ROOF | ROOF | 10552 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | WOOD | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4 | 57000 | MAINTAIN | GOOD
007 | Emerson | R01 | R01 | 00R | ROOF | ROOF | 8474 | SIPLAST PARADIENE 30 FR | 1990-08-01 | WOOD | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -16 | 45800 | MAINTAIN | GOOD
007 | Emerson | R02 | R02 | 00R | ROOF | ROOF | 9012 | SIPLAST PARADIENE 20 | 1992-08-01 | 2.3" ISO, 1" PERLITE, CON | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14 | 48700 | MAINTAIN | GOOD
007 | Emerson | R03 | R03 | 00R | ROOF | ROOF | 1326 | SIPLAST PARADIENE 30 FR | 1990-08-01 | WOOD | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -16 | 7200 | MAINTAIN | GOOD
007 | Emerson | R04 | R04 | 00R | ROOF | ROOF | 647 | SIPLAST PARADIENE 30 FR | 1990-08-01 | 1.5" ISO, 1.5" COMP INS, | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -16 | 3500 | MAINTAIN | GOOD
007 | Emerson | R05 | R05 | 00R | ROOF | ROOF | 1334 | SIPLAST PARADIENE 20 | 1992-08-01 | 2.3" ISO, 1" PERLITE, CON | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14 | 7200 | MAINTAIN | GOOD
007 | Emerson | R06 | R06 | 00R | ROOF | ROOF | 1148 | SIPLAST PARADIENE 30 FR | 1990-08-01 | WOOD | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -16 | 6200 | MAINTAIN | GOOD
007 | Emerson | R07 | R07 | 00R | ROOF | ROOF | 3511 | MANVILLE 4-PLY BUR | 1992-08-01 | WOOD | 34 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 3 | 20 | -14 | 19000 | REPAIR | FAIR
011 | Falk | R01 | R01 | 00R | ROOF | ROOF | 14687 | BUR W/ PEA GRAVEL | 1995-08-01 | METAL | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -11 | 79300 | MAINTAIN | GOOD
011 | Falk | R02 | R02 | 00R | ROOF | ROOF | 19145 | BUR W/ PEA GRAVEL | 1995-08-01 | WOOD | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -11 | 103400 | MAINTAIN | GOOD
011 | Falk | R03 | R03 | 00R | LMC | ROOF | 5946 | BUR W/ PEA GRAVEL | 1995-08-01 | UNKNOWN | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -11 | 32100 | MAINTAIN | GOOD
011 | Falk | R04 | R04 | 00R | ROOF | ROOF | 14270 | BUR W/ PEA GRAVEL | 1995-08-01 | WOOD | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -11 | 77100 | MAINTAIN | GOOD
011 | Falk | R05 | R05 | 00R | ROOF | ROOF | 5417 | BUR W/ PEA GRAVEL | 1995-08-01 | UNKNOWN | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -11 | 29300 | MAINTAIN | GOOD
011 | Falk | R06 | R06 | 00R | MUSIC | ROOF | 945 | BUR W/ PEA GRAVEL | 1995-08-01 | METAL | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -11 | 5100 | MAINTAIN | GOOD
011 | Falk | R07 | R07 | 00R | GYM | ROOF | 9858 | BUR W/ PEA GRAVEL | 1995-08-01 | METAL | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -11 | 53200 | MAINTAIN | GOOD
011 | Falk | R08 | R08 | 00R | ROOF | ROOF | 1750 | BUR W/ PEA GRAVEL | 1995-08-01 | METAL | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -11 | 9500 | MAINTAIN | GOOD
008 | Franklin | R01 | R01 | 00R | ROOF | ROOF | 2133 | UNKNOWN | 1965-08-01 | UNKNOWN | 61 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 15 | -46 | 11500 | REPAIR | POOR
008 | Franklin | R02 | R02 | 00R | ROOF | ROOF | 3019 | GEOFLEX-PIB | 1982-08-01 | WOOD | 44 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -24 | 16300 | REPAIR | POOR
008 | Franklin | R03 | R03 | 00R | ROOF | ROOF | 3033 | UNKNOWN | 1965-08-01 | UNKNOWN | 61 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 15 | -46 | 16400 | REPAIR | POOR
008 | Franklin | R04 | R04 | 00R | ROOF | ROOF | 2949 | MANVILLE DYNAGLAS FR | 1991-08-01 | CONCRETE | 35 | 3 | 3 | 0 | 3 | 0 | 3 | 0 | 15 | 20 | -15 | 15900 | REPLACE | POOR
008 | Franklin | R05 | R05 | 00R | ROOF | ROOF | 4336 | MANVILLE DYNAGLAS FR | 1991-08-01 | METAL | 35 | 3 | 3 | 3 | 3 | 0 | 3 | 0 | 21 | 20 | -15 | 23400 | REPLACE | POOR
008 | Franklin | R06 | R06 | 00R | ROOF | ROOF | 2340 | SIPLAST PARADIENE 20/30 FR | 1985-08-01 | METAL | 41 | 0 | 0 | 0 | 3 | 3 | 3 | 3 | 27 | 20 | -21 | 12600 | REPLACE | POOR
008 | Franklin | R07 | R07 | 00R | ROOF | ROOF | 149 | GEOFLEX-PIB | 1982-08-01 | WOOD | 44 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 8 | 20 | -24 | 800 | REPAIR | FAIR
008 | Franklin | R08 | R08 | 00R | ROOF | ROOF | 137 | UNKNOWN | 1965-08-01 | UNKNOWN | 61 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 8 | 15 | -46 | 700 | REPAIR | FAIR
008 | Franklin | R09 | R09 | 00R | ROOF | ROOF | 225 | UNKNOWN | 1965-08-01 | UNKNOWN | 61 | 3 | 0 | 0 | 3 | 3 | 3 | 5 | 37 | 15 | -46 | 1200 | REPLACE | POOR
008 | Franklin | R10 | R10 | 00R | ROOF | ROOF | 95 | COPPER | 1965-08-01 | UNKNOWN | 61 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 6 | 25 | -36 | 500 | REPAIR | FAIR
008 | Franklin | R11 | R11 | 00R | ROOF | ELECTRICAL | 229 | EPDM BALLAST | 1995-08-01 | WOOD | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | -16 | 900 | MAINTAIN | GOOD
009 | Glendale | R01 | R01 | 00R | R00F | ROOF | 13675 | FIRESTONE EPDM W/BALLAST | 1989-08-01 | METAL | 37 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 15 | -22 | 54700 | REPAIR | POOR
009 | Glendale | R02 | R02 | 00R | CANOPY | ROOF | 257 | SIPLAST PARADIENE 20/30 FR TG | 2003-08-01 | METAL | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -3 | 1400 | MAINTAIN | GOOD
009 | Glendale | R03 | R03 | 00R | LMC-GYM-ROOF | ROOF | 7101 | SIPLAST PARADIENE 20/30 FR TG | 2003-08-01 | METAL | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -3 | 38300 | MAINTAIN | GOOD
009 | Glendale | R04 | R04 | 00R | CANOPY | ROOF | 182 | SIPLAST PARADIENE 20/30 FR TG | 2003-08-01 | METAL | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -3 | 1000 | MAINTAIN | GOOD
009 | Glendale | R05 | R05 | 00R | CANOPY | ROOF | 277 | SIPLAST PARADIENE 20/30 FR TG | 2003-08-01 | METAL | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -3 | 1500 | MAINTAIN | GOOD
009 | Glendale | R06 | R06 | 00R | R00F | ROOF | 11236 | FIRESTONE EPDM W/BALLAST | 1989-08-01 | METAL | 37 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 15 | -22 | 44900 | REPAIR | POOR
009 | Glendale | R07 | R07 | 00R | R00F | ROOF | 11389 | FIRESTONE EPDM W/BALLAST | 1989-08-01 | METAL | 37 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 15 | -22 | 45600 | REPAIR | POOR
234 | Hamilton | C01 | C01 | 00R | CANOPY | CANOPY | 89 | SIPLAST PARADIENE 20/30 FR | 2000-08-01 | METAL | 26 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -6 | 500 | REPAIR | FAIR
234 | Hamilton | R01 | R01 | 00R | ROOF | LMC ROOF | 5480 | GAF GAFGLAS 4-PLY W/GRAV | 1991-08-01 | WOOD | 35 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | 20 | -15 | 29600 | REPAIR | FAIR
234 | Hamilton | R02 | R02 | 00R | ROOF | ROOF | 18570 | SIPLAST PARADIENE 20/30 FR | 2000-08-01 | WOOD | 26 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | 20 | -6 | 100300 | REPAIR | FAIR
234 | Hamilton | R03 | R03 | 00R | ROOF | ROOF | 4488 | SIPLAST PARADIENE 20/30 FR | 2000-08-01 | WOOD | 26 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | 20 | -6 | 24200 | REPAIR | FAIR
234 | Hamilton | R04 | R04 | 00R | ROOF | ROOF | 611 | SIPLAST COVER | 1997-08-01 | METAL | 29 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 7 | -22 | 3300 | REPAIR | FAIR
234 | Hamilton | R05 | R05 | 00R | ROOF | ROOF | 12150 | SCHULER 3FID MODIFIED | 1995-08-01 | WOOD | 31 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | 20 | -11 | 65600 | REPAIR | FAIR
234 | Hamilton | R06 | R06 | 00R | ROOF | ROOF | 1204 | SIPLAST PARADIENE 20/30 FR | 2000-08-01 | METAL | 26 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -6 | 6500 | REPAIR | FAIR
234 | Hamilton | R07 | R07 | 00R | ROOF | ROOF | 1876 | SIPLAST PARADIENE 20/30 FR | 2000-08-01 | METAL | 26 | 0 | 0 | 0 | 0 | 3 | 3 | 3 | 24 | 20 | -6 | 10100 | REPAIR | FAIR
234 | Hamilton | R08 | R08 | 00R | ROOF | ROOF | 2013 | SIPLAST PARADIENE 20/30 FR | 1989-08-01 | METAL | 37 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -17 | 10900 | REPAIR | FAIR
234 | Hamilton | R09 | R09 | 00R | ROOF | ROOF | 1667 | SIPLAST PARADIENE 20/30 FR | 2000-08-01 | METAL | 26 | 0 | 0 | 0 | 0 | 3 | 3 | 3 | 24 | 20 | -6 | 9000 | REPAIR | FAIR
234 | Hamilton | R10 | R10 | 00R | ROOF | ROOF | 214 | SIPLAST PARADIENE 20/30 FR | 1989-08-01 | METAL | 37 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -17 | 1200 | REPAIR | FAIR
234 | Hamilton | R11 | R11 | 00R | ROOF | ROOF | 772 | SIPLAST PARADIENE 20/30 FR | 1989-08-01 | METAL | 37 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -17 | 4200 | REPAIR | FAIR
234 | Hamilton | R12 | R12 | 00R | ROOF | ROOF | 7338 | SIPLAST PARADIENE 20/30 FR | 1989-08-01 | ACOUSTICAL-METAL | 37 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -17 | 39600 | REPAIR | FAIR
234 | Hamilton | R13 | R13 | 00R | ROOF | ROOF | 770 | SIPLAST PARADIENE 20/30 FR | 1989-08-01 | METAL | 37 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -17 | 4200 | REPAIR | FAIR
234 | Hamilton | R14 | R14 | 00R | ROOF | ROOF | 1416 | SIPLAST PARADIENE 20/30 FR | 1989-08-01 | METAL | 37 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -17 | 7600 | REPAIR | FAIR
234 | Hamilton | R15 | R15 | 00R | ROOF | ROOF | 217 | SIPLAST PARADIENE 20/30 FR | 1991-08-01 | METAL | 35 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -15 | 1200 | REPAIR | FAIR
234 | Hamilton | R16 | R16 | 00R | ROOF | ROOF | 1021 | SIPLAST PARADIENE 20/30 FR | 2000-08-01 | METAL | 26 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -6 | 5500 | REPAIR | FAIR
234 | Hamilton | R17 | R17 | 00R | ROOF | ROOF | 7366 | SIPLAST PARADIENE 20/30 FR | 1988-08-01 | METAL | 38 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 9 | 20 | -18 | 39800 | REPAIR | POOR
234 | Hamilton | R18 | R18 | 00R | ROOF | ROOF | 2780 | SIPLAST PARADIENE 20/30 FR | 1988-08-01 | METAL | 38 | 3 | 3 | 0 | 0 | 3 | 3 | 3 | 33 | 20 | -18 | 15000 | REPLACE | POOR
234 | Hamilton | R19 | R19 | 00R | ROOF | ROOF | 2812 | SIPLAST PARADIENE 20/30 FR | 1988-08-01 | METAL | 38 | 3 | 3 | 0 | 0 | 0 | 3 | 0 | 12 | 20 | -18 | 15200 | REPAIR | POOR
234 | Hamilton | R20 | R20 | 00R | ROOF | ROOF | 1306 | SIPLAST PARADIENE 20/30 FR | 2000-08-01 | METAL | 26 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -6 | 7100 | REPAIR | FAIR
234 | Hamilton | R21 | R21 | 00R | ROOF | ROOF | 4021 | SIPLAST PARADIENE 20/30 FR | 2000-08-01 | METAL | 26 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -6 | 21700 | REPAIR | FAIR
234 | Hamilton | R22 | R22 | 00R | ROOF | ROOF | 2130 | MANVILLE GLASPLY-IV 4-PLY | 1988-08-01 | WOOD | 38 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 6 | 20 | -18 | 11500 | REPAIR | FAIR
234 | Hamilton | R23 | R23 | 00R | ROOF | ROOF | 14277 | MANVILLE GLASPLY-IV 4-PLY | 1988-08-01 | WOOD | 38 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | 20 | -18 | 77100 | REPAIR | FAIR
234 | Hamilton | R24 | R24 | 00R | ROOF | ROOF | 1228 | BUR 4-PLY | 1962-08-01 | WOOD | 64 | 3 | 0 | 0 | 3 | 3 | 5 | 5 | 39 | 20 | -44 | 6600 | REPLACE | POOR
234 | Hamilton | R25 | R25 | 00R | ROOF | ROOF | 14560 | MANVILLE GLASPLY-IV 4-PLY | 1988-08-01 | WOOD | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -18 | 78600 | MAINTAIN | GOOD
012 | Hawthorne | R01 | R01 | 00R | ROOF | ROOF | 5624 | BUR W/ PEA GRAVEL | 1987-08-01 | METAL | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -19 | 30400 | MAINTAIN | GOOD
012 | Hawthorne | R02 | R02 | 00R | ROOF | ROOF | 22443 | BUR W/ PEA GRAVEL | 1987-08-01 | METAL | 39 | 0 | 1 | 0 | 3 | 0 | 0 | 0 | 4 | 20 | -19 | 121200 | REPAIR | FAIR
012 | Hawthorne | R03 | R03 | 00R | LOCKER | ROOF | 1940 | BUR W/ PEA GRAVEL | 1987-08-01 | METAL | 39 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 3 | 20 | -19 | 10500 | REPAIR | FAIR
012 | Hawthorne | R04 | R04 | 00R | GYM | ROOF | 4833 | BUR W/ PEA GRAVEL | 1987-08-01 | FINESTRA | 39 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -19 | 26100 | REPAIR | FAIR
012 | Hawthorne | R05 | R05 | 00R | LMC | ROOF | 5866 | BUR W/ PEA GRAVEL | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5 | 31700 | MAINTAIN | GOOD
012 | Hawthorne | R06 | R06 | 00R | ROOF | ROOF | 1231 | BUR W/ PEA GRAVEL | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5 | 6600 | MAINTAIN | GOOD
013 | Hoyt | R01 | R01 | 00R | ROOF | ROOF | 12818 | BUR W/ PEA GRAVEL | 1988-08-01 | UNKNOWN | 38 | 0 | 0 | 0 | 3 | 1 | 0 | 5 | 18 | 20 | -18 | 69200 | REPAIR | FAIR
013 | Hoyt | R02 | R02 | 00R | ROOF | ROOF | 6645 | BUR W/ PEA GRAVEL | 1988-08-01 | UNKNOWN | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -18 | 35900 | MAINTAIN | GOOD
013 | Hoyt | R03 | R03 | 00R | ROOF | ROOF | 5844 | BUR W/ PEA GRAVEL | 1988-08-01 | UNKNOWN | 38 | 0 | 0 | 0 | 3 | 1 | 0 | 5 | 18 | 20 | -18 | 31600 | REPAIR | FAIR
013 | Hoyt | R04 | R04 | 00R | GYM | ROOF | 4241 | BUR W/ PEA GRAVEL | 1988-08-01 | UNKNOWN | 38 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 3 | 20 | -18 | 22900 | REPAIR | FAIR
038 | Huegel | R01 | R01 | 00R | ROOF | ROOF | 4800 | CELOTEX-4-PLY-BUIT-UP | 1991-08-01 | METAL | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -15 | 25900 | MAINTAIN | GOOD
038 | Huegel | R02 | R02 | 00R | ROOF | ROOF | 832 | CELOTEX-4-PLY-BUIT-UP | 1991-08-01 | METAL | 35 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2 | 20 | -15 | 4500 | REPAIR | FAIR
038 | Huegel | R03 | R03 | 00R | ROOF | ROOF | 16349 | CELOTEX-4-PLY-BUIT-UP | 1991-08-01 | METAL | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -15 | 88300 | MAINTAIN | GOOD
038 | Huegel | R04 | R04 | 00R | ROOF | ROOF | 310 | CELOTEX-4-PLY-BUIT-UP | 1991-08-01 | METAL | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -15 | 1700 | MAINTAIN | GOOD
038 | Huegel | R05 | R05 | 00R | ROOF | ROOF | 5750 | CELOTEX-4-PLY-BUIT-UP | 1991-08-01 | METAL | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -15 | 31100 | MAINTAIN | GOOD
038 | Huegel | R06 | R06 | 00R | ROOF | ROOF | 461 | CELOTEX-4-PLY-BUIT-UP | 1991-08-01 | METAL | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -15 | 2500 | MAINTAIN | GOOD
038 | Huegel | R07 | R07 | 00R | ROOF | ROOF | 695 | CELOTEX-4-PLY-BUIT-UP | 1991-08-01 | METAL | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -15 | 3800 | MAINTAIN | GOOD
038 | Huegel | R08 | R08 | 00R | ROOF | ROOF | 229 | CELOTEX-4-PLY-BUIT-UP | 1991-08-01 | METAL | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -15 | 1200 | MAINTAIN | GOOD
038 | Huegel | R09 | R09 | 00R | ROOF | ROOF | 2135 | CELOTEX-4-PLY-BUIT-UP | 1991-08-01 | METAL | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -15 | 11500 | MAINTAIN | GOOD
038 | Huegel | R10 | R10 | 00R | ROOF | ROOF | 443 | MANVILLE GLASPLY-IV 4-PLY | 1993-08-01 | WOOD | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -13 | 2400 | MAINTAIN | GOOD
038 | Huegel | R11 | R11 | 00R | ROOF | ROOF | 2169 | MANVILLE GLASPLY-IV 4-PLY | 1993-08-01 | WOOD | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -13 | 11700 | MAINTAIN | GOOD
038 | Huegel | R12 | R12 | 00R | ROOF | ROOF | 1795 | MANVILLE GLASPLY-IV 4-PLY | 1993-08-01 | WOOD | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -13 | 9700 | MAINTAIN | GOOD
038 | Huegel | R13 | R13 | 00R | ROOF | ROOF | 419 | MANVILLE GLASPLY-IV 4-PLY | 1993-08-01 | WOOD | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -13 | 2300 | MAINTAIN | GOOD
038 | Huegel | R14 | R14 | 00R | ROOF | ROOF | 2217 | MANVILLE GLASPLY-IV 4-PLY | 1993-08-01 | WOOD | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -13 | 12000 | MAINTAIN | GOOD
038 | Huegel | R15 | R15 | 00R | ROOF | ROOF | 1469 | MANVILLE GLASPLY-IV 4-PLY | 1993-08-01 | WOOD | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -13 | 7900 | MAINTAIN | GOOD
038 | Huegel | R16 | R16 | 00R | ROOF | ROOF | 906 | MANVILLE GLASPLY-IV 4-PLY | 1993-08-01 | WOOD | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -13 | 4900 | MAINTAIN | GOOD
038 | Huegel | R17 | R17 | 00R | ROOF | ROOF | 1472 | MANVILLE GLASPLY-IV 4-PLY | 1993-08-01 | WOOD | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -13 | 7900 | MAINTAIN | GOOD
038 | Huegel | R18 | R18 | 00R | ROOF | ROOF | 2179 | MANVILLE GLASPLY-IV 4-PLY | 1993-08-01 | WOOD | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -13 | 11800 | MAINTAIN | GOOD
038 | Huegel | R19 | R19 | 00R | ROOF | ROOF | 9084 | MANVILLE GLASPLY-IV 4-PLY | 1993-08-01 | WOOD | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -13 | 49100 | MAINTAIN | GOOD
038 | Huegel | R20 | R20 | 00R | ROOF | ROOF | 1829 | MANVILLE GLASPLY-IV 4-PLY | 1993-08-01 | WOOD | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -13 | 9900 | MAINTAIN | GOOD
038 | Huegel | R21 | R21 | 00R | ROOF | ROOF | 819 | MANVILLE GLASPLY-IV 4-PLY | 1993-08-01 | WOOD | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -13 | 4400 | MAINTAIN | GOOD
038 | Huegel | R22 | R22 | 00R | ROOF | ROOF | 326 | CELOTEX-4-PLY-BUIT-UP | 1991-08-01 | METAL | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -15 | 1800 | MAINTAIN | GOOD
038 | Huegel | R23 | R23 | 00R | ROOF | ROOF | 651 | MANVILLE GLASPLY-IV 4-PLY | 1993-08-01 | WOOD | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -13 | 3500 | MAINTAIN | GOOD
038 | Huegel | R24 | R24 | 00R | ROOF | ROOF | 3377 | MANVILLE GLASPLY-IV 4-PLY | 1993-08-01 | WOOD | 33 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 6 | 20 | -13 | 18200 | REPAIR | FAIR
038 | Huegel | R25 | R25 | 00R | ROOF | ROOF | 650 | MANVILLE GLASPLY-IV 4-PLY | 1993-08-01 | WOOD | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -13 | 3500 | MAINTAIN | GOOD
245 | Jefferson | R01 | R01 | 00R | ROOF | ROOF | 12411 | SIPLAST PARADIENE 20/30 FR | 1989-08-01 | METAL | 37 | 3 | 3 | 0 | 0 | 0 | 3 | 0 | 12 | 20 | -17 | 67000 | REPAIR | POOR
245 | Jefferson | R02 | R02 | 00R | ROOF | ROOF | 16841 | SIPLAST PARADIENE 20/30 FR | 1989-08-01 | METAL | 37 | 3 | 5 | 0 | 0 | 3 | 3 | 3 | 35 | 20 | -17 | 90900 | REPLACE | POOR
245 | Jefferson | R03 | R03 | 00R | ROOF | ROOF | 10511 | SIPLAST PARADIENE 20/30 FR | 1989-08-01 | METAL | 37 | 3 | 3 | 0 | 0 | 0 | 3 | 0 | 12 | 20 | -17 | 56800 | REPAIR | POOR
245 | Jefferson | R04 | R04 | 00R | ROOF | ROOF | 1849 | SIPLAST PARADIENE 20/30 FR | 1989-08-01 | METAL | 37 | 3 | 3 | 0 | 0 | 0 | 3 | 0 | 12 | 20 | -17 | 10000 | REPAIR | POOR
245 | Jefferson | R05 | R05 | 00R | ROOF | ROOF | 6698 | SIPLAST PARADIENE 20/30 FR | 1989-08-01 | METAL | 37 | 3 | 5 | 0 | 0 | 3 | 3 | 3 | 35 | 20 | -17 | 36200 | REPLACE | POOR
245 | Jefferson | R06 | R06 | 00R | ROOF | ROOF | 1876 | SIPLAST PARADIENE 20/30 FR | 1989-08-01 | METAL | 37 | 3 | 3 | 0 | 0 | 0 | 3 | 0 | 12 | 20 | -17 | 10100 | REPAIR | POOR
036 | Kennedy | R01 | R01 | 00R | ROOF | ROOF | 6131 | SIPLAST PARADIENE 20/30 FR | 1987-08-01 | CONCRETE | 39 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | -19 | 33100 | REPAIR | FAIR
036 | Kennedy | R02 | R02 | 00R | ROOF | ROOF | 4877 | SIPLAST PARADIENE 20/30 FR | 2004-08-04 | CONCRETE | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -2 | 26300 | MAINTAIN | GOOD
036 | Kennedy | R03 | R03 | 00R | ROOF | ROOF | 4530 | MANVILLE GLASPLY-IV 4-PLY | 1991-08-01 | METAL | 35 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -15 | 24500 | REPAIR | FAIR
036 | Kennedy | R04 | R04 | 00R | ROOF | ROOF | 4701 | MANVILLE GLASPLY-IV 4-PLY | 1991-08-01 | METAL | 35 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -15 | 25400 | REPAIR | FAIR
036 | Kennedy | R05 | R05 | 00R | ROOF | ROOF | 6117 | SIPLAST PARADIENE 20/30 FR | 2004-08-04 | CONCRETE | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -2 | 33000 | MAINTAIN | GOOD
036 | Kennedy | R06 | R06 | 00R | ROOF | ROOF | 1323 | MANVILLE GLASPLY-IV 4-PLY | 1991-08-01 | METAL | 35 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 6 | 20 | -15 | 7100 | REPAIR | FAIR
036 | Kennedy | R07 | R07 | 00R | ROOF | ROOF | 7823 | MANVILLE GLASPLY-IV 4-PLY | 1991-08-01 | METAL | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -15 | 42200 | MAINTAIN | GOOD
142 | LaFollette | R01 | R01 | 00R | ROOF | ROOF | 12277 | UNKNOWN | 1994-08-01 | METAL | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -12 | 66300 | MAINTAIN | GOOD
142 | LaFollette | R02 | R02 | 00R | ROOF | ROOF | 304 | UNKNOWN | 1992-08-01 | METAL | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14 | 1600 | MAINTAIN | GOOD
142 | LaFollette | R03 | R03 | 00R | ROOF | ROOF | 6102 | SIPLAST PARADIENE 20/30 FR | 1986-08-01 | METAL | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -20 | 33000 | MAINTAIN | GOOD
142 | LaFollette | R04 | R04 | 00R | ROOF | ROOF | 5190 | MANVILLE GLASPLY-IV 4-PLY | 1993-08-01 | METAL | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -13 | 28000 | MAINTAIN | GOOD
142 | LaFollette | R05 | R05 | 00R | ROOF | ROOF | 8232 | MANVILLE GLASPLY-IV 4-PLY | 1993-08-01 | METAL | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -13 | 44500 | MAINTAIN | GOOD
142 | LaFollette | R06 | R06 | 00R | ROOF | ROOF | 5350 | MANVILLE GLASPLY-IV 4-PLY | 1993-08-01 | METAL | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -13 | 28900 | MAINTAIN | GOOD
142 | LaFollette | R07 | R07 | 00R | ROOF | ROOF | 8032 | SCHULLER 2FID MODIFIED | 1996-08-01 | METAL | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -10 | 43400 | MAINTAIN | GOOD
142 | LaFollette | R08 | R08 | 00R | ROOF | ROOF | 4154 | SCHULLER 2FID MODIFIED | 1996-08-01 | METAL | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -10 | 22400 | MAINTAIN | GOOD
142 | LaFollette | R09 | R09 | 00R | ROOF | ROOF | 814 | SARNIFIL | 1992-08-01 | Concrete | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14 | 4400 | MAINTAIN | GOOD
142 | LaFollette | R10 | R10 | 00R | ROOF | ROOF | 13724 | MANVILLE DYNAKAP FR | 1993-08-01 | METAL | 33 | 3 | 3 | 0 | 3 | 5 | 3 | 3 | 46 | 20 | -13 | 74100 | REPLACE | POOR
142 | LaFollette | R11 | R11 | 00R | ROOF | ROOF | 8368 | SCHULLER 2FID MODIFIED | 1996-08-01 | METAL | 30 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 20 | -10 | 45200 | REPAIR | FAIR
142 | LaFollette | R12 | R12 | 00R | ROOF | ROOF | 3794 | SCHULLER 2FID MODIFIED | 1996-08-01 | METAL | 30 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 20 | -10 | 20500 | REPAIR | FAIR
142 | LaFollette | R13 | R13 | 00R | ROOF | ROOF | 7280 | UNKNOWN | 1993-08-01 | METAL | 33 | 3 | 3 | 0 | 3 | 3 | 3 | 3 | 36 | 20 | -13 | 39300 | REPLACE | POOR
142 | LaFollette | R14 | R14 | 00R | ROOF | ROOF | 7267 | UNKNOWN | 1993-08-01 | METAL | 33 | 3 | 3 | 0 | 3 | 0 | 3 | 0 | 15 | 20 | -13 | 39200 | REPLACE | POOR
142 | LaFollette | R15 | R15 | 00R | ROOF | ROOF | 4628 | UNKNOWN | 1993-08-01 | METAL | 33 | 3 | 3 | 0 | 3 | 0 | 3 | 0 | 15 | 20 | -13 | 25000 | REPAIR | FAIR
142 | LaFollette | R16 | R16 | 00R | ROOF | ROOF | 7495 | UNKNOWN | 1965-08-01 | METAL | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -41 | 40500 | MAINTAIN | GOOD
142 | LaFollette | R17 | R17 | 00R | ROOF | ROOF | 9677 | SIPLAST PARADIENE 20/30 FR | 1992-08-01 | METAL | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14 | 52300 | MAINTAIN | GOOD
142 | LaFollette | R17A | R17A | 00R | ROOF | ROOF | 2782 | UNKNOWN | 1992-08-01 | METAL | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14 | 15000 | MAINTAIN | GOOD
142 | LaFollette | R17B | R17B | 00R | ROOF | ROOF | 11387 | SIPLAST PARADIENE 20/30 FR | 2001-08-01 | ACOUSTICAL-METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5 | 61500 | MAINTAIN | GOOD
142 | LaFollette | R18 | R18 | 00R | ROOF | ROOF | 5144 | UNKNOWN | 1997-08-01 | METAL | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -9 | 27800 | MAINTAIN | GOOD
142 | LaFollette | R19 | R19 | 00R | ROOF | ROOF | 15850 | MANVILLE DYNAGLAS FR | 1992-08-01 | METAL | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14 | 85600 | MAINTAIN | GOOD
142 | LaFollette | R20 | R20 | 00R | ROOF | ROOF | 25813 | GAF GAFGLAS MOD BIT | 1991-08-01 | METAL | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -15 | 139400 | MAINTAIN | GOOD
142 | LaFollette | R21 | R21 | 00R | ROOF | ROOF | 13989 | UNKNOWN | 1992-08-01 | METAL | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14 | 75500 | MAINTAIN | GOOD
142 | LaFollette | R22 | R22 | 00R | ROOF | ROOF | 24392 | UNKNOWN | 1992-08-01 | METAL | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14 | 131700 | MAINTAIN | GOOD
142 | LaFollette | R23 | R23 | 00R | ROOF | ROOF | 1456 | MANVILLE DYNAKAP FR | 1992-08-01 | METAL | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14 | 7900 | MAINTAIN | GOOD
142 | LaFollette | R24 | R24 | 00R | ROOF | ROOF | 982 | MANVILLE DYNAKAP FR | 1992-08-01 | 1.75" LT.WT. CONC OVER ME | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14 | 5300 | MAINTAIN | GOOD
142 | LaFollette | R25 | R25 | 00R | ROOF | ROOF | 2173 | MANVILLE DYNAKAP FR | 1992-08-01 | 1" LT.WT. CONC. OVER META | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14 | 11700 | MAINTAIN | GOOD
142 | LaFollette | R26 | R26 | 00R | ROOF | ROOF | 5570 | MANVILLE DYNAKAP FR | 1992-08-01 | METAL | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14 | 30100 | MAINTAIN | GOOD
142 | LaFollette | R27 | R27 | 00R | ROOF | ROOF | 343 | MANVILLE DYNAKAP FR | 1992-08-01 | METAL | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14 | 1900 | MAINTAIN | GOOD
142 | LaFollette | R28 | R28 | 00R | ROOF | ROOF | 2913 | MANVILLE DYNAKAP FR | 1992-08-01 | METAL | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14 | 15700 | MAINTAIN | GOOD
142 | LaFollette | R29 | R29 | 00R | ROOF | ROOF | 373 | MANVILLE DYNAKAP FR | 1992-08-01 | METAL | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14 | 2000 | MAINTAIN | GOOD
142 | LaFollette | R30 | R30 | 00R | ROOF | ROOF | 11239 | Tamko | 1995-08-01 | Metal | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -11 | 60700 | MAINTAIN | GOOD
142 | LaFollette | R31 | R31 | 00R | ROOF | ROOF | 435 | Tamko | 1995-08-01 | Metal | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -11 | 2300 | MAINTAIN | GOOD
142 | LaFollette | R32 | R32 | 00R | ROOF | ROOF | 6156 | SCHULLER 2FID MODIFIED | 1997-08-01 | METAL | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -9 | 33200 | MAINTAIN | GOOD
142 | LaFollette | R33 | R33 | 00R | ROOF | ROOF | 8118 | SCHULLER 2FID MODIFIED | 1997-08-01 | METAL | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -9 | 43800 | MAINTAIN | GOOD
142 | LaFollette | R34 | R34 | 00R | ROOF | ROOF | 4197 | UNKNOWN | 1992-08-01 | Metal | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14 | 22700 | MAINTAIN | GOOD
142 | LaFollette | R35 | R35 | 00R | ROOF | ROOF | 824 | SARNIFIL | 1992-08-01 | Metal | 34 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -14 | 4400 | REPAIR | FAIR
142 | LaFollette | R36 | R36 | 00R | ROOF | ROOF | 15874 | MANVILLE DYNAKAP FR | 1992-08-01 | METAL | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14 | 85700 | MAINTAIN | GOOD
142 | LaFollette | R37 | R37 | 00R | ROOF | TEAM ROOM | 3500 | SIPLAST PARADIENE 20/30 FR | 2003-08-01 | METAL | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -3 | 18900 | MAINTAIN | GOOD
142 | LaFollette | R38 | R38 | 00R | ROOF | MECHANICAL ROOM | 254 | SIPLAST PARADIENE 20/30 FR | 2003-08-01 | METAL | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -3 | 1400 | MAINTAIN | GOOD
142 | LaFollette | R39 | R39 | 00R | ROOF | CONCESSION | 4800 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4 | 25900 | MAINTAIN | GOOD
014 | Lakeview | C01 | C01 | 00R | ENTRANCE-CANOPY | CANOPY | 924 | BUR W/ PEA GRAVEL | 1991-08-01 | WOOD | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -15 | 5000 | MAINTAIN | GOOD
014 | Lakeview | C02 | C02 | 00R | RECEIVING-CANOPY | CANOPY | 546 | BUR W/ PEA GRAVEL | 1991-08-01 | WOOD | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -15 | 2900 | MAINTAIN | GOOD
014 | Lakeview | C03 | C03 | 00R | CANOPY | CANOPY | 276 | BUR W/ PEA GRAVEL | 1991-08-01 | WOOD | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -15 | 1500 | MAINTAIN | GOOD
014 | Lakeview | R01 | R01 | 00R | LOCKER | ROOF | 2071 | BUR W/ PEA GRAVEL | 1991-08-01 | WOOD | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -15 | 11200 | MAINTAIN | GOOD
014 | Lakeview | R02 | R02 | 00R | GYM | ROOF | 4471 | BUR W/ PEA GRAVEL | 1991-08-01 | WOOD | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -15 | 24100 | MAINTAIN | GOOD
014 | Lakeview | R03 | R03 | 00R | ROOF | ROOF | 7961 | BUR W/ PEA GRAVEL | 1991-08-01 | WOOD | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -15 | 43000 | MAINTAIN | GOOD
014 | Lakeview | R04 | R04 | 00R | ROOF | ROOF | 6697 | BUR W/ PEA GRAVEL | 1991-08-01 | WOOD | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -15 | 36200 | MAINTAIN | GOOD
014 | Lakeview | R05 | R05 | 00R | ROOF | ROOF | 6155 | BUR W/ PEA GRAVEL | 1991-08-01 | WOOD | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -15 | 33200 | MAINTAIN | GOOD
016 | Lapham | R01 | R01 | 00R | POOL | ROOF | 4792 | SIPLAST PARADIENE 20/30 FR | 2003-08-01 | CONCRETE | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -3 | 25900 | MAINTAIN | GOOD
016 | Lapham | R02 | R02 | 00R | ROOF | ROOF | 7213 | SIPLAST PARADIENE 20/30 FR | 1984-08-01 | CONCRETE | 42 | 3 | 3 | 0 | 3 | 0 | 5 | 0 | 17 | 20 | -22 | 39000 | REPLACE | POOR
016 | Lapham | R03 | R03 | 00R | ROOF | ROOF | 4207 | SIPLAST PARADIENE 20/30 FR | 1988-08-01 | CONCRETE | 38 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | -18 | 22700 | REPAIR | FAIR
016 | Lapham | R04 | R04 | 00R | CANOPY | CANOPY | 1128 | UNKNOWN | 1965-08-01 | UNKNOWN | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | -46 | 6100 | MAINTAIN | GOOD
016 | Lapham | R05 | R05 | 00R | ROOF | ROOF | 2957 | SIPLAST PARADIENE 20/30 FR | 1988-08-01 | CONCRETE | 38 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | -18 | 16000 | REPAIR | FAIR
016 | Lapham | R06 | R06 | 00R | ROOF | ROOF | 1061 | SIPLAST PARADIENE 20/30 FR | 1988-08-01 | CONCRETE | 38 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -18 | 5700 | REPAIR | FAIR
016 | Lapham | R07 | R07 | 00R | ROOF | ROOF | 5570 | SIPLAST PARADIENE 20/30 FR | 1988-08-01 | CONCRETE | 38 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | -18 | 30100 | REPAIR | FAIR
016 | Lapham | R08 | R08 | 00R | ROOF | ROOF | 5555 | SIPLAST PARADIENE 20/30 FR | 1988-08-01 | CONCRETE | 38 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -18 | 30000 | REPAIR | FAIR
016 | Lapham | R09 | R09 | 00R | ROOF | ROOF | 2780 | SIPLAST PARADIENE 20/30 FR | 1988-08-01 | CONCRETE | 38 | 3 | 3 | 0 | 0 | 0 | 3 | 0 | 12 | 20 | -18 | 15000 | REPAIR | FAIR
072 | Leopold | R01 | R01 | 00R | ROOF | ROOF | 3853 | SIPLAST PARADIENE 20/30 FR | 1986-08-01 | METAL | 40 | 0 | 5 | 3 | 0 | 0 | 3 | 0 | 14 | 20 | -20 | 20800 | REPAIR | POOR
072 | Leopold | R02 | R02 | 00R | ROOF | ROOF | 46 | SIPLAST PARADIENE 20/30 FR | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5 | 200 | MAINTAIN | GOOD
072 | Leopold | R03 | R03 | 00R | ROOF | ROOF | 12071 | SIPLAST PARADIENE 20/30 FR | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5 | 65200 | MAINTAIN | GOOD
072 | Leopold | R04 | R04 | 00R | ROOF | ROOF | 39 | SIPLAST PARADIENE 20/30 FR | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5 | 200 | MAINTAIN | GOOD
072 | Leopold | R05 | R05 | 00R | ROOF | ROOF | 2454 | MANVILLE DYNAKAP FR | 1990-08-01 | METAL | 36 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -16 | 13300 | REPAIR | FAIR
072 | Leopold | R06 | R06 | 00R | ROOF | ROOF | 4520 | MANVILLE DYNAKAP FR | 1990-08-01 | METAL | 36 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -16 | 24400 | REPAIR | FAIR
072 | Leopold | R07 | R07 | 00R | ROOF | ROOF | 7275 | SIPLAST PARADIENE 20/30 FR | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5 | 39300 | MAINTAIN | GOOD
072 | Leopold | R08 | R08 | 00R | ROOF | ROOF | 127 | SIPLAST PARADIENE 20/30 FR | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5 | 700 | MAINTAIN | GOOD
072 | Leopold | R09 | R09 | 00R | ROOF | ROOF | 16719 | SIPLAST PARADIENE 20/30 FR | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5 | 90300 | MAINTAIN | GOOD
072 | Leopold | R10 | R10 | 00R | ROOF | ROOF | 4898 | EPDM BALLAST | 2003-03-01 | METAL | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | -8 | 19600 | MAINTAIN | GOOD
072 | Leopold | R11 | R11 | 00R | ROOF | ROOF | 358 | EPDM BALLAST | 2003-03-01 | METAL | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | -8 | 1400 | MAINTAIN | GOOD
072 | Leopold | R12 | R12 | 00R | ROOF | LMC ROOF | 2422 | EPDM BALLAST | 2003-03-01 | METAL | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | -8 | 9700 | MAINTAIN | GOOD
072 | Leopold | R13 | R13 | 00R | ROOF | ROOF | 462 | EPDM BALLAST | 2003-03-01 | METAL | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | -8 | 1800 | MAINTAIN | GOOD
072 | Leopold | R14 | R14 | 00R | ROOF | ROOF | 7207 | EPDM BALLAST | 2003-03-01 | METAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 15 | 28800 | MAINTAIN | GOOD
037 | Lincoln | R01 | R01 | 00R | ROOF | ROOF | 7818 | CELOTEX-CELOPAL-I | 1986-08-01 | METAL | 40 | 0 | 5 | 0 | 0 | 0 | 3 | 0 | 8 | 20 | -20 | 42200 | REPAIR | POOR
037 | Lincoln | R02 | R02 | 00R | ROOF | ROOF | 6245 | CELOTEX-CELOPAL-I | 1986-08-01 | METAL | 40 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -20 | 33700 | REPAIR | POOR
037 | Lincoln | R03 | R03 | 00R | ROOF | ROOF | 6397 | CELOTEX-CELOPAL-I | 1986-08-01 | METAL | 40 | 1 | 3 | 0 | 0 | 0 | 3 | 0 | 8 | 20 | -20 | 34500 | REPAIR | POOR
037 | Lincoln | R04 | R04 | 00R | ROOF | ROOF | 3004 | CELOTEX-CELOPAL-I | 1986-08-01 | METAL | 40 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -20 | 16200 | REPAIR | POOR
037 | Lincoln | R05 | R05 | 00R | ADDITION - ROOF | ROOF | 5916 | BUR W/ PEA GRAVEL | 2000-08-01 | METAL | 26 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -6 | 31900 | REPAIR | FAIR
037 | Lincoln | R06 | R06 | 00R | ROOF | ROOF | 5272 | CELOTEX-CELOPAL-I | 1986-08-01 | METAL | 40 | 0 | 3 | 1 | 3 | 0 | 3 | 0 | 11 | 20 | -20 | 28500 | REPAIR | POOR
037 | Lincoln | R07 | R07 | 00R | ROOF | ROOF | 4941 | CELOTEX-CELOPAL-I | 1986-08-01 | METAL | 40 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | -20 | 26700 | REPAIR | POOR
037 | Lincoln | R08 | R08 | 00R | ROOF | ROOF | 6951 | CELOTEX-CELOPAL-I | 1986-08-01 | METAL | 40 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -20 | 37500 | REPAIR | POOR
037 | Lincoln | R09 | R09 | 00R | ROOF | ROOF | 5728 | CELOTEX-CELOPAL-I | 1986-08-01 | METAL | 40 | 0 | 3 | 2 | 2 | 0 | 3 | 0 | 12 | 20 | -20 | 30900 | REPAIR | POOR
037 | Lincoln | R10 | R10 | 00R | ROOF | ROOF | 4047 | CELOTEX-CELOPAL-I | 1986-08-01 | METAL | 40 | 0 | 2 | 0 | 0 | 0 | 4 | 0 | 6 | 20 | -20 | 21900 | REPAIR | POOR
037 | Lincoln | R11 | R11 | 00R | ROOF | ROOF | 11011 | CELOTEX-CELOPAL-I | 1986-08-01 | METAL | 40 | 0 | 1 | 0 | 0 | 0 | 4 | 0 | 5 | 20 | -20 | 59500 | REPAIR | POOR
071 | Lindbergh | R01 | R01 | 00R | ROOF | ROOF | 10297 | SIPLAST PARADIENE 20/30 FR | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5 | 55600 | MAINTAIN | GOOD
071 | Lindbergh | R02 | R02 | 00R | ROOF | ROOF | 15558 | SIPLAST PARADIENE 20/30 FR | 1987-08-01 | METAL | 39 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 42 | 20 | -19 | 84000 | REPLACE | POOR
071 | Lindbergh | R03 | R03 | 00R | ROOF | ROOF | 3486 | SIPLAST PARADIENE 20/30 FR | 1986-08-01 | METAL | 40 | 3 | 3 | 3 | 3 | 0 | 3 | 0 | 21 | 20 | -20 | 18800 | REPLACE | POOR
071 | Lindbergh | R04 | R04 | 00R | ROOF | ROOF | 4474 | SIPLAST PARADIENE 20/30 FR | 1984-08-01 | METAL | 42 | 3 | 3 | 0 | 3 | 0 | 3 | 0 | 15 | 20 | -22 | 24200 | REPAIR | POOR
019 | Lowell | C01 | C01 | 00R | MAPLE ST. ENTRANCE CANOPY | CANOPY | 0 | REMOVED | 2003-08-01 | UNKNOWN | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -23 | 0 | MAINTAIN | GOOD
019 | Lowell | R01 | R01 | 00R | ROOF | ROOF | 795 | SIPLAST PARADIENE 20/30 FR | 1985-08-01 | WOOD | 41 | 0 | 3 | 2 | 0 | 0 | 3 | 0 | 10 | 20 | -21 | 4300 | REPAIR | FAIR
019 | Lowell | R02 | R02 | 00R | ROOF | ROOF | 1678 | SIPLAST PARADIENE 20/30 FR | 1985-08-01 | WOOD | 41 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -21 | 9100 | REPAIR | FAIR
019 | Lowell | R03 | R03 | 00R | ROOF | ROOF | 2934 | SIPLAST PARADIENE 20/30 FR | 1985-08-01 | WOOD | 41 | 0 | 3 | 3 | 0 | 0 | 3 | 0 | 12 | 20 | -21 | 15800 | REPAIR | FAIR
019 | Lowell | R04 | R04 | 00R | ROOF | ROOF | 567 | SIPLAST PARADIENE 20/30 FR | 1985-08-01 | WOOD | 41 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -21 | 3100 | REPAIR | FAIR
019 | Lowell | R05 | R05 | 00R | ROOF | ROOF | 799 | SIPLAST PARADIENE 20/30 FR | 1985-08-01 | WOOD | 41 | 0 | 3 | 3 | 0 | 0 | 3 | 0 | 12 | 20 | -21 | 4300 | REPAIR | FAIR
019 | Lowell | R06 | R06 | 00R | ROOF | ROOF | 1707 | SIPLAST PARADIENE 20/30 FR | 1985-08-01 | WOOD | 41 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -21 | 9200 | REPAIR | FAIR
019 | Lowell | R07 | R07 | 00R | ROOF | ROOF | 726 | CLAY TILE WITH FELT BELOW | 1995-08-01 | WOOD | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 44 | 10900 | MAINTAIN | GOOD
019 | Lowell | R08 | R08 | 00R | ROOF | ROOF | 79 | CLAY TILE | 1927-08-01 | WOOD | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | -24 | 1200 | MAINTAIN | GOOD
019 | Lowell | R08A | R08A | 00R | ROOF | ROOF | 251 | CLAY TILE | 1927-08-01 | WOOD | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | -24 | 3800 | MAINTAIN | GOOD
019 | Lowell | R09 | R09 | 00R | ROOF | ROOF | 233 | CLAY TILE | 1927-08-01 | WOOD | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | -24 | 3500 | MAINTAIN | GOOD
019 | Lowell | R10 | R10 | 00R | ROOF | ROOF | 250 | CLAY TILE | 1927-08-01 | WOOD | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | -24 | 3800 | MAINTAIN | GOOD
019 | Lowell | R11 | R11 | 00R | ROOF | ROOF | 246 | CLAY TILE | 1927-08-01 | WOOD | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | -24 | 3700 | MAINTAIN | GOOD
019 | Lowell | R12 | R12 | 00R | ROOF | ROOF | 14560 | SIPLAST PARADIENE 20/30 FR | 1985-08-01 | CONCRETE | 41 | 3 | 3 | 0 | 0 | 0 | 3 | 0 | 12 | 20 | -21 | 78600 | REPAIR | FAIR
019 | Lowell | R13 | R13 | 00R | ROOF | ROOF | 1433 | SIPLAST PARADIENE 20/30 FR | 1985-08-01 | CONCRETE | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -21 | 7700 | MAINTAIN | GOOD
019 | Lowell | R14 | R14 | 00R | ROOF | ROOF | 1071 | SIPLAST PARADIENE 20/30 FR | 1985-08-01 | CONCRETE | 41 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -21 | 5800 | REPAIR | FAIR
019 | Lowell | R15 | R15 | 00R | ROOF | ROOF | 4018 | EPDM/LG BOARD | 1985-08-01 | CONCRETE | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | -26 | 16100 | MAINTAIN | GOOD
019 | Lowell | R16 | R16 | 00R | STAIR ROOF | ROOF | 441 | CONCRETE TILE | 1985-08-01 | CONCRETE | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -21 | 6600 | MAINTAIN | GOOD
019 | Lowell | R17 | R17 | 00R | TRACTOR STORAGE ROOF | ROOF | 139 | UNKNOWN | 1991-08-01 | UNKNOWN | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | -20 | 800 | MAINTAIN | GOOD
145 | Memorial | R01 | R01 | 00R | ROOF | GARAGE ROOF | 1450 | EPDM BALLAST | 1988-08-01 | METAL | 38 | 3 | 3 | 3 | 3 | 0 | 5 | 0 | 23 | 15 | -23 | 5800 | REPLACE | POOR
145 | Memorial | R02 | R02 | 00R | ROOF | RECEIVING ROOF | 419 | EPDM BALLAST | 1988-08-01 | METAL | 38 | 3 | 3 | 3 | 3 | 0 | 5 | 0 | 23 | 15 | -23 | 1700 | REPLACE | POOR
145 | Memorial | R03 | R03 | 00R | ROOF | BOILER ROOM ROOF | 2356 | BUR 4-PLY | 1965-08-01 | METAL | 61 | 0 | 3 | 3 | 3 | 0 | 5 | 0 | 17 | 20 | -41 | 12700 | REPLACE | POOR
145 | Memorial | R04 | R04 | 00R | ROOF | SPEC GYM ROOF | 19961 | TAMKO 704 | 1995-08-01 | METAL | 31 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 6 | 20 | -11 | 107800 | REPAIR | FAIR
145 | Memorial | R05 | R05 | 00R | ROOF | STAGE ROOF | 2379 | MANVILLE DYNAKAP FR | 1987-08-01 | METAL | 39 | 3 | 3 | 0 | 0 | 0 | 3 | 0 | 12 | 20 | -19 | 12800 | REPAIR | FAIR
145 | Memorial | R06 | R06 | 00R | ROOF | AUDITORIUM ROOF | 8145 | MANVILLE DYNAKAP FR | 1987-08-01 | METAL | 39 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | -19 | 44000 | REPAIR | FAIR
145 | Memorial | R07 | R07 | 00R | ROOF | MUSIC WING ROOF | 6536 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4 | 35300 | MAINTAIN | GOOD
145 | Memorial | R08 | R08 | 00R | ROOF | ROOF | 132 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4 | 700 | MAINTAIN | GOOD
145 | Memorial | R09 | R09 | 00R | ROOF | COMMONS ROOF | 6604 | MANVILLE DYNAKAP FR | 1996-08-01 | METAL | 30 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -10 | 35700 | REPAIR | FAIR
145 | Memorial | R10 | R10 | 00R | ROOF | PLANITARIUM | 1103 | MANVILLE DYNAKAP FR | 1996-08-01 | METAL | 30 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -10 | 6000 | REPAIR | FAIR
145 | Memorial | R11 | R11 | 00R | ROOF | ROOF | 2646 | MANVILLE DYNAKAP FR | 1996-08-01 | METAL | 30 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -10 | 14300 | REPAIR | FAIR
145 | Memorial | R12 | R12 | 00R | ROOF | ROOF | 1772 | MANVILLE DYNAKAP FR | 1996-08-01 | METAL | 30 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -10 | 9600 | REPAIR | FAIR
145 | Memorial | R13 | R13 | 00R | ROOF | ROOF | 680 | MANVILLE DYNAKAP FR | 1996-08-01 | METAL | 30 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -10 | 3700 | REPAIR | FAIR
145 | Memorial | R14 | R14 | 00R | ROOF | ROOF | 18026 | MANVILLE DYNAKAP FR | 1987-08-01 | METAL | 39 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -19 | 97300 | REPAIR | FAIR
145 | Memorial | R15 | R15 | 00R | ROOF | ROOF | 11429 | MANVILLE DYNAKAP FR | 1987-08-01 | METAL | 39 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -19 | 61700 | REPAIR | FAIR
145 | Memorial | R16 | R16 | 00R | ROOF | ROOF | 17660 | MANVILLE DYNAKAP FR | 1988-08-01 | METAL | 38 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -18 | 95400 | REPAIR | FAIR
145 | Memorial | R17 | R17 | 00R | ROOF | ROOF | 3663 | MANVILLE DYNAKAP FR | 1988-08-01 | METAL | 38 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -18 | 19800 | REPAIR | FAIR
145 | Memorial | R18 | R18 | 00R | ROOF | ROOF | 2726 | MANVILLE DYNAKAP FR | 1988-08-01 | METAL | 38 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -18 | 14700 | REPAIR | FAIR
145 | Memorial | R19 | R19 | 00R | ROOF | ROOF | 9456 | SIPLAST PARADIENE 20/30 FR | 1996-08-01 | METAL | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -10 | 51100 | MAINTAIN | GOOD
145 | Memorial | R20 | R20 | 00R | ROOF | ROOF | 12811 | MANVILLE DYNAKAP FR | 1996-08-01 | METAL | 30 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -10 | 69200 | REPAIR | FAIR
145 | Memorial | R21 | R21 | 00R | ROOF | ROOF | 16007 | MODIFIED BIT. | 1995-08-01 | METAL | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -11 | 86400 | MAINTAIN | GOOD
145 | Memorial | R22 | R22 | 00R | ROOF | ROOF | 8393 | SIPLAST PARADIENE 20/30 FR | 1999-08-01 | METAL | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -7 | 45300 | MAINTAIN | GOOD
145 | Memorial | R23 | R23 | 00R | ROOF | FH ENTRANCE | 500 | MANVILLE DYNAKAP FR | 1992-08-01 | METAL | 34 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -14 | 2700 | REPAIR | FAIR
145 | Memorial | R24 | R24 | 00R | ROOF | FH | 28009 | MANVILLE DYNAKAP FR | 1992-08-01 | METAL | 34 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -14 | 151200 | REPAIR | FAIR
145 | Memorial | R25 | R25 | 00R | ROOF | FH MECHANICAL | 3124 | MANVILLE DYNAKAP FR | 1992-08-01 | METAL | 34 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -14 | 16900 | REPAIR | FAIR
145 | Memorial | R26 | R26 | 00R | ROOF | FH LOCKER RM | 5061 | MANVILLE DYNAKAP FR | 1992-08-01 | METAL | 34 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -14 | 27300 | REPAIR | FAIR
145 | Memorial | R27 | R27 | 00R | ROOF | SPORTS TRAINING ROOM | 1273 | SIPLAST PARADIENE 20/30 FR | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5 | 6900 | MAINTAIN | GOOD
145 | Memorial | R28 | R28 | 00R | ROOF | ROOF | 7070 | SIPLAST PARADIENE 20/30 FR | 1996-08-01 | METAL | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -10 | 38200 | MAINTAIN | GOOD
145 | Memorial | R29 | R29 | 00R | ROOF | ROOF | 8312 | SIPLAST PARADIENE 20/30 FR | 1996-08-01 | METAL | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -10 | 44900 | MAINTAIN | GOOD
145 | Memorial | R30 | R30 | 00R | ROOF | ROOF | 4476 | SIPLAST PARADIENE 20/30 FR | 1999-08-01 | METAL | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -7 | 24200 | MAINTAIN | GOOD
145 | Memorial | R31 | R31 | 00R | ROOF | ROOF | 7988 | SIPLAST PARADIENE 20/30 FR | 1999-08-01 | METAL | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -7 | 43100 | MAINTAIN | GOOD
145 | Memorial | R32 | R32 | 00R | ROOF | ROOF | 11555 | SIPLAST PARADIENE 20/30 FR | 1996-08-01 | METAL | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -10 | 62400 | MAINTAIN | GOOD
145 | Memorial | R33 | R33 | 00R | ROOF | ROOF | 1811 | MANVILLE DYNAKAP FR | 1987-08-01 | METAL | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -19 | 9800 | MAINTAIN | GOOD
145 | Memorial | R34 | R34 | 00R | ROOF | ROOF | 457 | SIPLAST PARADIENE 20/30 FR | 1987-08-01 | METAL | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -19 | 2500 | MAINTAIN | GOOD
145 | Memorial | R35 | R35 | 00R | ROOF | NEIGHBORHOOD ROOM | 1327 | SIPLAST PARADIENE 20/30 FR | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5 | 7200 | MAINTAIN | GOOD
145 | Memorial | R36 | R36 | 00R | ROOF | ROOF | 280 | SIPLAST PARADIENE 20/30 FR | 1996-08-01 | METAL | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -10 | 1500 | MAINTAIN | GOOD
145 | Memorial | R37 | R37 | 00R | ROOF | ROOF | 17524 | MANVILLE DYNAKAP FR | 1987-08-01 | METAL | 39 | 0 | 3 | 3 | 0 | 0 | 3 | 0 | 12 | 20 | -19 | 94600 | REPAIR | FAIR
145 | Memorial | R38 | R38 | 00R | ROOF | ROOF | 11048 | MANVILLE DYNAKAP FR | 1988-08-01 | METAL | 38 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -18 | 59700 | REPAIR | FAIR
145 | Memorial | R39 | R39 | 00R | ROOF | MANSFIELD | 3787 | SIPLAST PARADIENE 20/30 FR | 1999-08-01 | METAL | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -7 | 20400 | MAINTAIN | GOOD
145 | Memorial | R40 | R40 | 00R | ROOF | MANSFIELD | 5040 | SIPLAST PARADIENE 20/30 FR | 1999-08-01 | METAL | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -7 | 27200 | MAINTAIN | GOOD
145 | Memorial | R41 | R41 | 00R | ROOF | MANSFIELD | 2568 | SIPLAST PARADIENE 20/30 FR | 1999-08-01 | METAL | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -7 | 13900 | MAINTAIN | GOOD
145 | Memorial | R42 | R42 | 00R | ROOF | CONCESSION | 800 | SIPLAST PARADIENE 20/30 FR | 1998-08-01 | METAL | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -8 | 4300 | MAINTAIN | GOOD
145 | Memorial | R43 | R43 | 00R | ROOF | MANSFIELD | 3804 | SIPLAST PARADIENE 20/30 FR | 1999-08-01 | METAL | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -7 | 20500 | MAINTAIN | GOOD
021 | Mendota | C01 | C01 | 00R | CANOPY | CANOPY | 63 | TARMAC SBS FR | 1991-08-01 | WOOD-METAL | 35 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 6 | 20 | -15 | 300 | REPAIR | FAIR
021 | Mendota | R01 | R01 | 00R | ROOF | ROOF | 5206 | SIPLAST PARADIENE 20/30 FR | 2003-08-01 | METAL | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -3 | 28100 | MAINTAIN | GOOD
021 | Mendota | R02 | R02 | 00R | ROOF | ROOF | 582 | MANVILLE DYNAKAP FR | 1987-08-01 | CONCRETE | 39 | 5 | 0 | 5 | 3 | 0 | 5 | 0 | 28 | 20 | -19 | 3100 | REPLACE | POOR
021 | Mendota | R03 | R03 | 00R | ROOF | ROOF | 4545 | MANVILLE DYNAKAP FR | 1987-08-01 | WOOD | 39 | 5 | 3 | 5 | 3 | 3 | 5 | 5 | 56 | 20 | -19 | 24500 | REPLACE | POOR
021 | Mendota | R04 | R04 | 00R | ROOF | ROOF | 9829 | MANVILLE DYNAKAP FR | 1987-08-01 | WOOD | 39 | 3 | 3 | 5 | 3 | 3 | 5 | 5 | 52 | 20 | -19 | 53100 | REPLACE | POOR
021 | Mendota | R05 | R05 | 00R | ROOF | ROOF | 6639 | MANVILLE DYNAKAP FR | 1987-08-01 | WOOD | 39 | 5 | 3 | 5 | 3 | 0 | 5 | 0 | 31 | 20 | -19 | 35900 | REPLACE | POOR
021 | Mendota | R06 | R06 | 00R | GYM ROOF | ROOF | 3454 | SIPLAST PARADIENE 20/30 FR TG | 2003-08-01 | METAL | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -3 | 18700 | MAINTAIN | GOOD
021 | Mendota | R07 | R07 | 00R | ROOF | ROOF | 1282 | MANVILLE DYNAKAP FR | 1987-08-01 | WOOD | 39 | 5 | 0 | 0 | 3 | 0 | 5 | 0 | 18 | 20 | -19 | 6900 | REPLACE | POOR
021 | Mendota | R08 | R08 | 00R | ROOF | ROOF | 12114 | TARMAC SBS FR | 1991-08-01 | WOOD-METAL | 35 | 3 | 5 | 0 | 5 | 0 | 3 | 0 | 19 | 20 | -15 | 65400 | REPLACE | POOR
021 | Mendota | R09 | R09 | 00R | ROOF | ROOF | 2084 | TARMAC SBS FR | 1991-08-01 | WOOD-METAL | 35 | 3 | 3 | 0 | 3 | 0 | 3 | 0 | 15 | 20 | -15 | 11300 | REPLACE | POOR
022 | Midvale | R01 | R01 | 00R | GYM ROOF | ROOF | 7634 | CELOTEX-CELOPAL-I | 1985-08-01 | GYPSUM | 41 | 0 | 3 | 3 | 0 | 0 | 3 | 0 | 12 | 20 | -21 | 41200 | REPAIR | POOR
022 | Midvale | R02 | R02 | 00R | ROOF | ROOF | 8593 | SIPLAST PARADIENE 20/30 FR | 1981-08-01 | UNKNOWN | 45 | 3 | 5 | 3 | 3 | 0 | 3 | 0 | 23 | 20 | -25 | 46400 | REPLACE | POOR
022 | Midvale | R03 | R03 | 00R | ROOF | ROOF | 9763 | CELOTEX CP101C | 1986-08-01 | UNKNOWN | 40 | 5 | 5 | 3 | 3 | 2 | 5 | 5 | 49 | 20 | -20 | 52700 | REPLACE | POOR
017 | Muir | C01 | C01 | 00R | CANOPY | CANOPY | 116 | MANVILLE 4-PLY BUR | 1992-08-01 | METAL | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14 | 600 | MAINTAIN | GOOD
017 | Muir | C02 | C02 | 00R | CANOPY | CANOPY | 119 | MANVILLE 4-PLY BUR | 1992-08-01 | METAL | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14 | 600 | MAINTAIN | GOOD
017 | Muir | R01 | R01 | 00R | ROOF | ROOF | 5056 | MANVILLE 4-PLY BUR | 1992-08-01 | METAL | 34 | 0 | 0 | 0 | 1 | 0 | 3 | 0 | 4 | 20 | -14 | 27300 | REPAIR | FAIR
017 | Muir | R02 | R02 | 00R | ROOF | ROOF | 709 | MANVILLE 4-PLY BUR | 1992-08-01 | METAL | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14 | 3800 | MAINTAIN | GOOD
017 | Muir | R03 | R03 | 00R | ROOF | ROOF | 645 | MANVILLE 4-PLY BUR | 1992-08-01 | METAL | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14 | 3500 | MAINTAIN | GOOD
017 | Muir | R04 | R04 | 00R | ROOF | ROOF | 4603 | MANVILLE 4-PLY BUR | 1992-08-01 | METAL | 34 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 3 | 20 | -14 | 24900 | REPAIR | FAIR
017 | Muir | R05 | R05 | 00R | ROOF | ROOF | 269 | MANVILLE 4-PLY BUR | 1992-08-01 | METAL | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14 | 1500 | MAINTAIN | GOOD
017 | Muir | R06 | R06 | 00R | ROOF | ROOF | 1627 | SIPLAST PARADIENE 20/30 FR | 1998-08-01 | CONCRETE | 28 | 3 | 0 | 0 | 0 | 0 | 4 | 0 | 10 | 20 | -8 | 8800 | REPLACE | POOR
017 | Muir | R07 | R07 | 00R | ROOF | ROOF | 719 | MANVILLE 4-PLY BUR | 1992-08-01 | METAL | 34 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 3 | 20 | -14 | 3900 | REPAIR | FAIR
017 | Muir | R08 | R08 | 00R | ROOF | ROOF | 627 | MANVILLE 4-PLY BUR | 1992-08-01 | METAL | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14 | 3400 | MAINTAIN | GOOD
017 | Muir | R09 | R09 | 00R | ROOF | ROOF | 5107 | MANVILLE 4-PLY BUR | 1992-08-01 | METAL | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14 | 27600 | MAINTAIN | GOOD
017 | Muir | R10 | R10 | 00R | ROOF | ROOF | 4555 | SIPLAST PARADIENE 20/30 FR | 1988-08-01 | WOOD FIBER | 38 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 20 | -18 | 24600 | REPAIR | FAIR
017 | Muir | R11 | R11 | 00R | ROOF | ROOF | 13903 | SIPLAST PARADIENE 20/30 FR | 1988-08-01 | METAL | 38 | 3 | 3 | 0 | 0 | 0 | 0 | 0 | 9 | 20 | -18 | 75100 | REPAIR | FAIR
017 | Muir | R12 | R12 | 00R | ROOF | ROOF | 13913 | SIPLAST PARADIENE 20/30 FR | 1988-08-01 | METAL | 38 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -18 | 75100 | REPAIR | FAIR
017 | Muir | R13 | R13 | 00R | ROOF | ROOF | 3932 | MANVILLE 4-PLY BUR | 1992-08-01 | METAL | 34 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -14 | 21200 | REPAIR | FAIR
017 | Muir | R14 | R14 | 00R | ROOF | ROOF | 5682 | SIPLAST PARADIENE 20/30 FR | 1988-08-01 | METAL | 38 | 0 | 1 | 0 | 0 | 0 | 3 | 0 | 4 | 20 | -18 | 30700 | REPAIR | FAIR
017 | Muir | R15 | R15 | 00R | ROOF | ROOF | 315 | UNKNOWN | 1989-08-01 | METAL | 37 | 0 | 5 | 1 | 0 | 0 | 3 | 0 | 10 | 15 | -22 | 1700 | REPAIR | FAIR
017 | Muir | R16 | R16 | 00R | 1ST ADDITION ROOF | ROOF | 5323 | UNKNOWN | 1989-08-01 | METAL | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | -22 | 28700 | MAINTAIN | GOOD
220 | O'Keeffe | R01 | R01 | 00R | ROOF | ROOF | 7710 | SCHULLER 2FID MODIFIED | 1995-08-01 | UNKNOWN | 31 | 0 | 3 | 3 | 3 | 0 | 3 | 0 | 15 | 20 | -11 | 41600 | REPLACE | POOR
220 | O'Keeffe | R02 | R02 | 00R | ROOF | ROOF | 10105 | SCHULLER 2FID MODIFIED | 1996-08-01 | UNKNOWN | 30 | 3 | 3 | 0 | 0 | 0 | 0 | 0 | 9 | 20 | -10 | 54600 | REPAIR | FAIR
220 | O'Keeffe | R03 | R03 | 00R | ROOF | ROOF | 1648 | SIPLAST PARADIENE 20/30 FR | 1985-08-01 | METAL | 41 | 0 | 3 | 3 | 0 | 0 | 3 | 0 | 12 | 20 | -21 | 8900 | REPAIR | FAIR
220 | O'Keeffe | R04 | R04 | 00R | ROOF | ROOF | 3445 | EPDM BALLAST | 1986-08-01 | WOOD | 40 | 0 | 0 | 0 | 3 | 3 | 3 | 5 | 31 | 15 | -25 | 13800 | REPLACE | POOR
220 | O'Keeffe | R05 | R05 | 00R | ROOF | ROOF | 2849 | SIPLAST PARADIENE 20/30 FR | 1986-08-01 | METAL | 40 | 3 | 3 | 0 | 0 | 0 | 3 | 0 | 12 | 20 | -20 | 15400 | REPAIR | FAIR
220 | O'Keeffe | R06 | R06 | 00R | ROOF | ROOF | 7091 | MANVILLE 4-PLY BUR | 1994-08-01 | METAL | 32 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -12 | 38300 | REPAIR | FAIR
220 | O'Keeffe | R07 | R07 | 00R | ROOF | ROOF | 1139 | SIPLAST PARADIENE 20/30 FR | 1998-08-01 | UNKNOWN | 28 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -8 | 6200 | REPAIR | FAIR
220 | O'Keeffe | R08 | R08 | 00R | ROOF | ROOF | 1323 | SIPLAST PARADIENE 20/30 FR | 1998-08-01 | PRECAST CONCRETE | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -8 | 7100 | MAINTAIN | GOOD
220 | O'Keeffe | R09 | R09 | 00R | ROOF | ROOF | 1684 | SCHULLER 2FID MODIFIED | 1996-08-01 | UNKNOWN | 30 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -10 | 9100 | REPAIR | FAIR
220 | O'Keeffe | R10 | R10 | 00R | ROOF | ROOF | 1752 | SIPLAST PARADIENE 20/30 FR | 1998-08-01 | PRECAST CONCRETE | 28 | 3 | 0 | 0 | 0 | 0 | 1 | 0 | 7 | 20 | -8 | 9500 | REPAIR | FAIR
220 | O'Keeffe | R11 | R11 | 00R | ROOF | ROOF | 7090 | SIPLAST PARADIENE 20/30 FR | 1998-08-01 | METAL | 28 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -8 | 38300 | REPAIR | FAIR
220 | O'Keeffe | R12 | R12 | 00R | ROOF | ROOF | 4871 | SIPLAST PARADIENE 20/30 FR | 1998-08-01 | METAL | 28 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -8 | 26300 | REPAIR | FAIR
220 | O'Keeffe | R13 | R13 | 00R | ROOF | ROOF | 3257 | SIPLAST PARADIENE 20/30 FR | 1998-08-01 | PRECAST CONCRETE | 28 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -8 | 17600 | REPAIR | FAIR
220 | O'Keeffe | R14 | R14 | 00R | ROOF | ROOF | 2128 | SIPLAST PARADIENE 20/30 FR | 1998-08-01 | UNKNOWN | 28 | 5 | 0 | 0 | 0 | 0 | 3 | 0 | 13 | 20 | -8 | 11500 | REPAIR | FAIR
220 | O'Keeffe | R15 | R15 | 00R | MECH. ROOM | ROOF | 748 | SIPLAST PARADIENE 20/30 FR | 1998-08-01 | METAL | 28 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -8 | 4000 | REPAIR | FAIR
220 | O'Keeffe | R16 | R16 | 00R | FIELD HOUSE NORTHWEST | ROOF | 2877 | SIPLAST PARADIENE 20/30 FR | 1990-08-01 | CEMENTITIOUS WOOD FIBER | 36 | 0 | 3 | 0 | 0 | 0 | 5 | 0 | 8 | 20 | -16 | 15500 | REPAIR | FAIR
220 | O'Keeffe | R17 | R17 | 00R | FIELD HOUSE NORTH EAST | ROOF | 2959 | SIPLAST PARADIENE 20/30 FR | 1990-08-01 | CEMENTITIOUS WOOD FIBER | 36 | 0 | 3 | 0 | 0 | 0 | 5 | 0 | 8 | 20 | -16 | 16000 | REPAIR | FAIR
220 | O'Keeffe | R18 | R18 | 00R | FIELD HOUSE SOUTH EAST | ROOF | 2892 | SIPLAST PARADIENE 20/30 FR | 1990-08-01 | CEMENTITIOUS WOOD FIBER | 36 | 0 | 3 | 0 | 0 | 0 | 5 | 0 | 8 | 20 | -16 | 15600 | REPAIR | FAIR
220 | O'Keeffe | R19 | R19 | 00R | FIELD HOUSE SOUTH WEST | ROOF | 2798 | SIPLAST PARADIENE 20/30 FR | 1990-08-01 | CEMENTITIOUS WOOD FIBER | 36 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | 20 | -16 | 15100 | REPAIR | FAIR
220 | O'Keeffe | R20 | R20 | 00R | ROOF | ROOF | 2146 | SIPLAST PARADIENE 20/30 FR | 1998-08-01 | UNKNOWN | 28 | 5 | 0 | 0 | 0 | 0 | 3 | 0 | 13 | 20 | -8 | 11600 | REPAIR | FAIR
220 | O'Keeffe | R21 | R21 | 00R | ROOF | ROOF | 7246 | SIPLAST PARADIENE 20/30 FR | 1998-08-01 | METAL | 28 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -8 | 39100 | REPAIR | FAIR
220 | O'Keeffe | R22 | R22 | 00R | ROOF | ROOF | 662 | SIPLAST PARADIENE 20/30 FR | 1998-08-01 | METAL | 28 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -8 | 3600 | REPAIR | FAIR
305 | PFLAUM | C01 | C01 | 00R | MAIN ENTRANCE CANOPY | CANOPY | 60 | STANDING SEAM GALV/ALUM | 1987-08-01 | NONE | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | -14 | 300 | MAINTAIN | GOOD
305 | PFLAUM | C02 | C02 | 00R | CARPENTER CANOPY | CANOPY | 154 | STANDING SEAM GALV/ALUM | 1987-08-01 | NONE | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | -14 | 800 | MAINTAIN | GOOD
305 | PFLAUM | C03 | C03 | 00R | MAINTENANCE CANOPY | CANOPY | 154 | STANDING SEAM GALV/ALUM | 1987-08-01 | NONE | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | -14 | 800 | MAINTAIN | GOOD
305 | PFLAUM | C04 | C04 | 00R | PAINT CANOPY | CANOPY | 169 | STANDING SEAM GALV/ALUM | 1987-08-01 | NONE | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | -14 | 900 | MAINTAIN | GOOD
305 | PFLAUM | C05 | C05 | 00R | SM. ENGINE CANOPY | CANOPY | 95 | STANDING SEAM GALV/ALUM | 1987-08-01 | NONE | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | -14 | 500 | MAINTAIN | GOOD
305 | PFLAUM | R01 | R01 | 00R | ROOF | ROOF | 50067 | STANDING SEAM GALV/ALUM | 1987-08-01 | METAL/SKYLIGHTS | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | -14 | 270400 | MAINTAIN | GOOD
305 | PFLAUM | R02 | R02 | 00R | LOADING DOCK ROOF | ROOF | 2622 | METAL | 1991-08-01 | NONE | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | -10 | 14200 | MAINTAIN | GOOD
305 | PFLAUM | R03 | R03 | 00R | FPC UPPER ROOF | ROOF | 12355 | METAL | 1991-08-01 | NONE | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | -10 | 66700 | MAINTAIN | GOOD
305 | PFLAUM | R04 | R04 | 00R | FPC LOWER ROOF | ROOF | 4202 | METAL | 1991-08-01 | NONE | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | -10 | 22700 | MAINTAIN | GOOD
026 | Randall | R01 | R01 | 00R | ROOF | ROOF | 2561 | MANVILLE 4GIG | 1998-08-01 | WOOD | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -8 | 13800 | MAINTAIN | GOOD
026 | Randall | R02 | R02 | 00R | ROOF | ROOF | 4757 | MANVILLE 4GIG | 1998-08-01 | WOOD | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -8 | 25700 | MAINTAIN | GOOD
026 | Randall | R03 | R03 | 00R | ROOF | ROOF | 1342 | CONCRETE TILE | 1998-08-01 | WOOD | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 22 | 20100 | MAINTAIN | GOOD
026 | Randall | R04 | R04 | 00R | ROOF | ROOF | 4991 | CONCRETE TILE | 1998-08-01 | WOOD | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 22 | 74900 | MAINTAIN | GOOD
026 | Randall | R05 | R05 | 00R | ROOF | ROOF | 3304 | CONCRETE TILE | 1998-08-01 | WOOD | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 22 | 49600 | MAINTAIN | GOOD
026 | Randall | R06 | R06 | 00R | ROOF | ROOF | 4992 | CONCRETE TILE | 1998-08-01 | WOOD | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 22 | 74900 | MAINTAIN | GOOD
026 | Randall | R07 | R07 | 00R | ROOF | ROOF | 1342 | CONCRETE TILE | 1998-08-01 | WOOD | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 22 | 20100 | MAINTAIN | GOOD
053 | Sandburg | R01 | R01 | 00R | ROOF | ROOF | 38590 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | 1/2" WOOD FIBER, (2) LAYE | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4 | 208400 | MAINTAIN | GOOD
053 | Sandburg | R02 | R02 | 00R | GYM ROOF | ROOF | 4586 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | 1/2" WOOD FIBER, (2) LAYE | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4 | 24800 | MAINTAIN | GOOD
053 | Sandburg | R03 | R03 | 00R | ADDITION | ROOF | 5011 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | 1/2" WOOD FIBER, (2) LAYE | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4 | 27100 | MAINTAIN | GOOD
053 | Sandburg | R04 | R04 | 00R | RELOCATABLE ROOF | ROOF | 860 | BUR 4-PLY | 2003-08-01 | PLYWOOD DECK | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -3 | 4600 | MAINTAIN | GOOD
242 | Sennett | C01 | C01 | 00R | Main Entrance Canopy | Canopy | 153 | MANVILLE DYNAKAP FR,2.2" | 1989-08-01 | STEEL/CONCRETE | 37 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -17 | 800 | REPAIR | POOR
242 | Sennett | C02 | C02 | 00R | Rear Entrance | Canopy | 158 | MANVILLE DYNAKAP FR,2.2" | 1989-08-01 | STEEL/CONCRETE | 37 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -17 | 900 | REPAIR | POOR
242 | Sennett | R01 | R01 | 00R | Old Cafeteria | ROOF | 875 | BUR 4-PLY | 1980-08-01 | METAL | 46 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -26 | 4700 | REPAIR | POOR
242 | Sennett | R02 | R02 | 00R | GYM NW AREA | ROOF | 1575 | MANVILLE DYNAKAP FR,2.2" | 1989-08-01 | STEEL/CONCRETE | 37 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 6 | 20 | -17 | 8500 | REPAIR | POOR
242 | Sennett | R03 | R03 | 00R | GYM ROOF SW | ROOF | 1573 | MANVILLE DYNAKAP FR,2.2" | 1989-08-01 | STEEL/CONCRETE | 37 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | -17 | 8500 | REPAIR | POOR
242 | Sennett | R04 | R04 | 00R | GYM ROOF NE | ROOF | 1584 | MANVILLE DYNAKAP FR, 2.2" | 1989-08-01 | STEEL/CONCRETE | 37 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | -17 | 8600 | REPAIR | POOR
242 | Sennett | R05 | R05 | 00R | GYM ROOF SE | ROOF | 1583 | MANVILLE DYNAKAP FR,2.2" | 1989-08-01 | STEEL/CONCRETE | 37 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | -17 | 8500 | REPAIR | POOR
242 | Sennett | R06 | R06 | 00R | UPPER MECH NORTH | ROOF | 1413 | MANVILLE DYNAKAP FR,2.2" | 1989-08-01 | STEEL/CONCRETE | 37 | 3 | 3 | 0 | 3 | 0 | 3 | 0 | 15 | 20 | -17 | 7600 | REPLACE | POOR
242 | Sennett | R07 | R07 | 00R | UPPER MECH SOUTH | ROOF | 1406 | MANVILLE DYNAKAP FR,2.2" | 1989-08-01 | STEEL/CONCRETE | 37 | 3 | 3 | 3 | 3 | 0 | 3 | 0 | 21 | 20 | -17 | 7600 | REPLACE | POOR
242 | Sennett | R08 | R08 | 00R | CLASSROOM NW | ROOF | 2763 | MANVILLE DYNAKAP FR,2.2" | 1989-08-01 | STEEL/CONCRETE | 37 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | -17 | 14900 | REPAIR | POOR
242 | Sennett | R09 | R09 | 00R | ROOF | ROOF | 2293 | MANVILLE DYNAKAP FR,2.2" | 1989-08-01 | STEEL/CONCRETE | 37 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | -17 | 12400 | REPAIR | POOR
242 | Sennett | R10 | R10 | 00R | ROOF | ROOF | 2744 | MANVILLE DYNAKAP FR, 2.2" | 1989-08-01 | STEEL/CONCRETE | 37 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | -17 | 14800 | REPAIR | POOR
242 | Sennett | R11 | R11 | 00R | ROOF | ROOF | 2634 | MANVILLE DYNAKAP FR,2.2" | 1989-08-01 | STEEL/CONCRETE | 37 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 6 | 20 | -17 | 14200 | REPAIR | POOR
242 | Sennett | R12 | R12 | 00R | ROOF | ROOF | 2210 | MANVILLE DYNAKAP FR,2.2" | 1989-08-01 | STEEL/CONCRETE | 37 | 3 | 3 | 0 | 3 | 0 | 3 | 0 | 15 | 20 | -17 | 11900 | REPLACE | POOR
242 | Sennett | R13 | R13 | 00R | ROOF | ROOF | 2617 | MANVILLE DYNAKAP FR,2.2" | 1989-08-01 | STEEL/CONCRETE | 37 | 3 | 3 | 0 | 3 | 0 | 3 | 0 | 15 | 20 | -17 | 14100 | REPLACE | POOR
242 | Sennett | R14 | R14 | 00R | ROOF | ROOF | 2713 | MANVILLE DYNAKAP FR, 2.2" | 1989-08-01 | STEEL/CONCRETE | 37 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | -17 | 14700 | REPAIR | POOR
242 | Sennett | R15 | R15 | 00R | ROOF | ROOF | 2243 | MANVILLE DYNAKAP FR, 2.2" | 1989-08-01 | STEEL/CONCRETE | 37 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 6 | 20 | -17 | 12100 | REPAIR | POOR
242 | Sennett | R16 | R16 | 00R | ROOF | ROOF | 2691 | MANVILLE DYNAKAP FR,2.2" | 1989-08-01 | STEEL/CONCRETE | 37 | 0 | 5 | 0 | 3 | 0 | 3 | 0 | 11 | 20 | -17 | 14500 | REPAIR | POOR
242 | Sennett | R17 | R17 | 00R | ROOF | ROOF | 2708 | MANVILLE DYNAKAP FR,2.2" | 1989-08-01 | STEEL/CONCRETE | 37 | 0 | 3 | 0 | 3 | 3 | 3 | 3 | 30 | 20 | -17 | 14600 | REPLACE | POOR
242 | Sennett | R18 | R18 | 00R | ROOF | ROOF | 2250 | MANVILLE DYNAKAP FR, 2.2" | 1989-08-01 | STEEL/CONCRETE | 37 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 6 | 20 | -17 | 12200 | REPAIR | POOR
242 | Sennett | R19 | R19 | 00R | ROOF | ROOF | 2676 | MANVILLE DYNAKAP FR,2.2" | 1989-08-01 | STEEL/CONCRETE | 37 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | -17 | 14500 | REPAIR | POOR
242 | Sennett | R20 | R20 | 00R | ROOF | ROOF | 1276 | MANVILLE DYNAKAP FR, 2.2" | 1989-08-01 | STEEL/CONCRETE | 37 | 3 | 3 | 0 | 3 | 0 | 3 | 0 | 15 | 20 | -17 | 6900 | REPLACE | POOR
242 | Sennett | R21 | R21 | 00R | ROOF | ROOF | 2917 | MANVILLE DYNAGLAS DYNABAS | 1992-08-01 | METAL | 34 | 0 | 5 | 0 | 3 | 0 | 3 | 0 | 11 | 20 | -14 | 15800 | REPAIR | FAIR
242 | Sennett | R22 | R22 | 00R | ROOF | ROOF | 3050 | MANVILLE DYNAGLAS DYNABAS | 1992-08-01 | METAL | 34 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | -14 | 16500 | REPAIR | FAIR
242 | Sennett | R23 | R23 | 00R | ROOF | ROOF | 3067 | MANVILLE DYNAGLAS DYNABAS | 1992-08-01 | METAL | 34 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | -14 | 16600 | REPAIR | FAIR
242 | Sennett | R24 | R24 | 00R | ROOF | ROOF | 2879 | MANVILLE DYNAGLAS DYNABAS | 1992-08-01 | METAL | 34 | 0 | 3 | 3 | 3 | 0 | 3 | 0 | 15 | 20 | -14 | 15500 | REPLACE | POOR
228 | Sherman | C01 | C01 | 00R | CANOPY | CANOPY | 122 | COAL TAR | 1960-08-01 | WOOD | 66 | 0 | 5 | 0 | 3 | 0 | 5 | 0 | 13 | 20 | -46 | 700 | REPLACE | POOR
228 | Sherman | C02 | C02 | 00R | CANOPY | CANOPY | 128 | COAL TAR | 1960-08-01 | WOOD | 66 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 8 | 20 | -46 | 700 | REPAIR | POOR
228 | Sherman | R01 | R01 | 00R | ROOF | ROOF | 9931 | TEMPORARY ROOF | 1996-08-01 | METAL | 30 | 0 | 5 | 1 | 3 | 0 | 3 | 0 | 13 | 7 | -23 | 53600 | REPAIR | POOR
228 | Sherman | R02 | R02 | 00R | ROOF | ROOF | 796 | SIPLAST PARADIENE 20/30 FR | 2003-08-03 | METAL | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -3 | 4300 | MAINTAIN | GOOD
228 | Sherman | R02A | R02A | 00R | ELEVATOR ROOF | ROOF | 622 | SIPLAST PARADIENE 20/30 FR | 2003-08-01 | METAL | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -3 | 3400 | MAINTAIN | GOOD
228 | Sherman | R03 | R03 | 00R | ROOF | ROOF | 160 | SIPLAST PARADIENE 20/30 FR | 2003-08-03 | METAL | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -3 | 900 | MAINTAIN | GOOD
228 | Sherman | R04 | R04 | 00R | ROOF | ROOF | 7434 | FIRESTONE-(MECH-FASTENED) | 1994-08-01 | WOOD | 32 | 3 | 0 | 0 | 0 | 3 | 0 | 5 | 31 | 15 | -17 | 29700 | REPLACE | POOR
228 | Sherman | R05 | R05 | 00R | ROOF | ROOF | 423 | SIPLAST PARADIENE 20/30 FR | 1993-08-01 | METAL | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -13 | 2300 | MAINTAIN | GOOD
228 | Sherman | R06 | R06 | 00R | ROOF | ROOF | 1956 | SIPLAST PARADIENE 20/30 FR | 1993-08-01 | METAL | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -13 | 10600 | MAINTAIN | GOOD
228 | Sherman | R07 | R07 | 00R | ROOF | ROOF | 4904 | SIPLAST PARADIENE 20/30 FR | 1993-08-01 | METAL | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -13 | 26500 | MAINTAIN | GOOD
228 | Sherman | R08 | R08 | 00R | ROOF | ROOF | 1205 | SIPLAST PARADIENE 20/30 FR | 1993-08-01 | METAL | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -13 | 6500 | MAINTAIN | GOOD
228 | Sherman | R09 | R09 | 00R | ROOF | ROOF | 48 | SIPLAST PARADIENE 20/30 FR | 1993-08-01 | METAL | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -13 | 300 | MAINTAIN | GOOD
228 | Sherman | R10 | R10 | 00R | ROOF | ROOF | 718 | SIPLAST PARADIENE 20/30 FR | 1993-08-01 | METAL | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -13 | 3900 | MAINTAIN | GOOD
228 | Sherman | R11 | R11 | 00R | ROOF | ROOF | 4835 | SIPLAST PARADIENE 20/30 FR | 1993-08-01 | METAL | 33 | 3 | 3 | 0 | 0 | 0 | 0 | 0 | 9 | 20 | -13 | 26100 | REPAIR | FAIR
228 | Sherman | R12 | R12 | 00R | ROOF | ROOF | 704 | SIPLAST PARADIENE 20/30 FR | 1993-08-01 | METAL | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -13 | 3800 | MAINTAIN | GOOD
228 | Sherman | R13 | R13 | 00R | ROOF | ROOF | 7480 | SIPLAST PARADIENE 20/30 FR | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5 | 40400 | MAINTAIN | GOOD
228 | Sherman | R14 | R14 | 00R | ROOF | ROOF | 5662 | MANVILLE DYNAGLAS FR | 1995-08-01 | METAL | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -11 | 30600 | MAINTAIN | GOOD
228 | Sherman | R15 | R15 | 00R | ROOF | ROOF | 1815 | SIPLAST PARADIENE 20/30 FR | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5 | 9800 | MAINTAIN | GOOD
228 | Sherman | R16 | R16 | 00R | ROOF | ROOF | 7923 | SIPLAST PARADIENE 20/30 FR | 2001-08-01 | CONCRETE | 25 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 20 | -5 | 42800 | REPAIR | FAIR
228 | Sherman | R17 | R17 | 00R | ROOF | ROOF | 160 | SIPLAST PARADIENE 20/30 FR | 1993-08-01 | METAL | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -13 | 900 | MAINTAIN | GOOD
228 | Sherman | R18 | R18 | 00R | ELEVATOR ROOF | ROOF | 82 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4 | 400 | MAINTAIN | GOOD
228 | Sherman | R19 | R19 | 00R | ROOF | ROOF | 13216 | MODIFIED BIT. | 1996-08-01 | WOOD | 30 | 3 | 3 | 3 | 0 | 0 | 0 | 0 | 15 | 20 | -10 | 71400 | REPAIR | FAIR
228 | Sherman | R20 | R20 | 00R | LMC ROOF | ROOF | 7013 | BUR 4-PLY | 1992-08-01 | WOOD | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14 | 37900 | MAINTAIN | GOOD
029 | Shorewood | C01 | C01 | 00R | CANOPY | CANOPY | 223 | GAF GAFGLAS 104G | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4 | 1200 | MAINTAIN | GOOD
029 | Shorewood | C02 | C02 | 00R | CANOPY | CANOPY | 27 | GAF GAFGLAS 104G | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4 | 100 | MAINTAIN | GOOD
029 | Shorewood | C03 | C03 | 00R | CANOPY | CANOPY | 122 | GAF GAFGLAS 104G | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4 | 700 | MAINTAIN | GOOD
029 | Shorewood | C04 | C04 | 00R | CANOPY | CANOPY | 122 | SIPLAST PARADIENE 20/30 FR | 2003-08-01 | METAL | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -3 | 700 | MAINTAIN | GOOD
029 | Shorewood | C05 | C05 | 00R | CANOPY | CANOPY | 30 | SIPLAST PARADIENE 20/30 FR | 2003-08-01 | METAL | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -3 | 200 | MAINTAIN | GOOD
029 | Shorewood | R01 | R01 | 00R | ROOF | ROOF | 9354 | GAF GAFGLAS 104G | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4 | 50500 | MAINTAIN | GOOD
029 | Shorewood | R02 | R02 | 00R | ROOF | ROOF | 3672 | 3-PLY TEMP | 1996-08-01 | METAL | 30 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 7 | -23 | 19800 | REPAIR | POOR
029 | Shorewood | R03 | R03 | 00R | ROOF | ROOF | 3017 | 3-PLY TEMP | 1996-08-01 | METAL | 30 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 7 | -23 | 16300 | REPAIR | POOR
029 | Shorewood | R04 | R04 | 00R | ROOF | ROOF | 1842 | SIPLAST PARADIENE 20/30 FR | 2003-08-01 | METAL | 23 | 3 | 3 | 0 | 0 | 0 | 3 | 0 | 12 | 20 | -3 | 9900 | REPAIR | FAIR
029 | Shorewood | R05 | R05 | 00R | ROOF | ROOF | 8383 | SIPLAST PARADIENE 20/30 FR | 2003-08-01 | METAL | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -3 | 45300 | MAINTAIN | GOOD
029 | Shorewood | R06 | R06 | 00R | ROOF | ROOF | 5358 | SIPLAST PARADIENE 20/30 FR | 2003-08-01 | METAL | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -3 | 28900 | MAINTAIN | GOOD
029 | Shorewood | R07 | R07 | 00R | ROOF | ROOF | 3664 | GRACE GRM-500 | 1984-08-01 | TAMKO 15# FELT, 2.2" ISOC | 42 | 3 | 3 | 0 | 3 | 3 | 3 | 5 | 40 | 20 | -22 | 19800 | REPLACE | POOR
029 | Shorewood | R08 | R08 | 00R | ROOF | ROOF | 8664 | MODIFIED BIT. | 1990-08-01 | METAL | 36 | 3 | 3 | 3 | 0 | 3 | 3 | 3 | 39 | 20 | -16 | 46800 | REPLACE | POOR
231 | Spring Harbor | C01 | C01 | 00R | CANOPY ROOF | ROOF | 508 | MANVILLE GLASPLY-IV 4-PLY | 1987-08-01 | METAL | 39 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 6 | 20 | -19 | 2700 | REPAIR | FAIR
231 | Spring Harbor | R01 | R01 | 00R | ROOF | ROOF | 9182 | MANVILLE GLASPLY-IV 4-PLY | 1987-08-01 | METAL | 39 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 6 | 20 | -19 | 49600 | REPAIR | FAIR
231 | Spring Harbor | R02 | R02 | 00R | ROOF | ROOF | 11482 | MANVILLE GLASPLY-IV 4-PLY | 1987-08-01 | METAL | 39 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 6 | 20 | -19 | 62000 | REPAIR | FAIR
231 | Spring Harbor | R03 | R03 | 00R | LMC ROOF | ROOF | 4489 | MANVILLE GLASPLY-IV 4-PLY | 1987-08-01 | METAL | 39 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 6 | 20 | -19 | 24200 | REPAIR | FAIR
231 | Spring Harbor | R04 | R04 | 00R | GYMNASIUM ROOF | ROOF | 5201 | MANVILLE GLASPLY-IV 4-PLY | 1987-08-01 | METAL | 39 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 6 | 20 | -19 | 28100 | REPAIR | FAIR
032 | Stephens | R01 | R01 | 00R | ROOF | ROOF | 19806 | MANVILLE-DYNAKAP | 1986-08-01 | METAL | 40 | 0 | 0 | 0 | 3 | 3 | 3 | 3 | 27 | 20 | -20 | 118836 | REPLACE | FAIR
032 | Stephens | R02 | R02 | 00R | ROOF | ROOF | 16559 | MANVILLE-DYNAKAP | 1986-08-01 | METAL | 40 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 6 | 20 | -20 | 99354 | REPAIR | FAIR
032 | Stephens | R03 | R03 | 00R | GYM ROOF | ROOF | 4382 | MANVILLE-DYNAKAP | 1986-08-01 | METAL | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -20 | 26292 | MAINTAIN | GOOD
032 | Stephens | R04 | R04 | 00R | LMC ROOF AREA | ROOF | 8723 | MANVILLE-DYNAKAP-3CIG | 1990-08-01 | UNKNOWN | 36 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 6 | 20 | -16 | 52338 | REPAIR | FAIR
032 | Stephens | R05 | R05 | 00R | ROOF | ROOF | 517 | GAF GAFGLAS 104G | 1993-08-01 | UNKNOWN | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -13 | 2800 | MAINTAIN | GOOD
032 | Stephens | R06 | R06 | 00R | ROOF | ROOF | 2754 | GAF GAFGLAS 104G | 1993-08-01 | UNKNOWN | 33 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 6 | 20 | -13 | 14900 | REPAIR | FAIR
032 | Stephens | R07 | R07 | 00R | GYM ROOF | ROOF | 8779 | GAF GAFGLAS 104G | 1993-08-01 | UNKNOWN | 33 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -13 | 47400 | REPAIR | FAIR
032 | Stephens | R08 | R08 | 00R | ROOF | ROOF | 16237 | GAF GAFGLAS 104G | 1993-08-01 | UNKNOWN | 33 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 6 | 20 | -13 | 87700 | REPAIR | FAIR
032 | Stephens | R09 | R09 | 00R | ROOF | ROOF | 1808 | GAF GAFGLAS 104G | 1993-08-01 | UNKNOWN | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -13 | 9800 | MAINTAIN | GOOD
023 | Thoreau | R01 | R01 | 00R | ROOF | ROOF | 4752 | SIPLAST PARADIENE 20/30 FR | 1985-08-01 | 2.2" ISOCYANURATE, (2) LA | 41 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | -21 | 25700 | REPAIR | POOR
023 | Thoreau | R02 | R02 | 00R | ROOF | ROOF | 2622 | SIPLAST PARADIENE 20/30 FR | 1985-08-01 | 2.2" ISOCYANURATE, (2) LA | 41 | 0 | 3 | 0 | 3 | 0 | 5 | 0 | 11 | 20 | -21 | 14200 | REPLACE | POOR
023 | Thoreau | R03 | R03 | 00R | ROOF | ROOF | 588 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4 | 3200 | MAINTAIN | GOOD
023 | Thoreau | R04 | R04 | 00R | ROOF | ROOF | 8948 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4 | 48300 | MAINTAIN | GOOD
023 | Thoreau | R05 | R05 | 00R | ROOF | ROOF | 5454 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4 | 29500 | MAINTAIN | GOOD
023 | Thoreau | R06 | R06 | 00R | ROOF | ROOF | 916 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4 | 4900 | MAINTAIN | GOOD
023 | Thoreau | R07 | R07 | 00R | ROOF | ROOF | 5516 | SIPLAST PARADIENE 20/30 FR | 1985-08-01 | 2.2" ISOCYANURATE, (2) LA | 41 | 0 | 3 | 3 | 0 | 0 | 3 | 0 | 12 | 20 | -21 | 29800 | REPAIR | POOR
023 | Thoreau | R08 | R08 | 00R | ROOF | ROOF | 5196 | FIRESTONE EPDM W/BALLAST | 1992-08-01 | METAL | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | -19 | 20800 | MAINTAIN | POOR
023 | Thoreau | R09 | R09 | 00R | ROOF | ROOF | 1766 | FIRESTONE EPDM W/BALLAST | 1992-08-01 | METAL | 34 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 15 | -19 | 7100 | REPAIR | POOR
023 | Thoreau | R10 | R10 | 00R | ROOF | ROOF | 2204 | SIPLAST PARADIENE 20/30 FR | 1992-08-01 | METAL | 34 | 0 | 3 | 0 | 3 | 0 | 5 | 0 | 11 | 20 | -14 | 11900 | REPLACE | POOR
225 | Toki | C01 | C01 | 00R | CANOPY | CANOPY | 133 | UNKNOWN | 1962-08-01 | UNKNOWN | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | -49 | 700 | MAINTAIN | GOOD
225 | Toki | C02 | C02 | 00R | CANOPY | CANOPY | 24 | UNKNOWN | 1962-08-01 | UNKNOWN | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | -49 | 100 | MAINTAIN | GOOD
225 | Toki | C03 | C03 | 00R | CANOPY | CANOPY | 40 | SIPLAST PARADIENE 20/30 FR | 1999-08-01 | METAL | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -7 | 200 | MAINTAIN | GOOD
225 | Toki | R01 | R01 | 00R | ROOF | ROOF | 4788 | SIPLAST PARADIENE 20/30 FR | 2003-08-01 | METAL | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -3 | 25900 | MAINTAIN | GOOD
225 | Toki | R02 | R02 | 00R | ROOF | ROOF | 10335 | SIPLAST PARADIENE 20/30 FR | 1999-08-01 | METAL | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -7 | 55800 | MAINTAIN | GOOD
225 | Toki | R03 | R03 | 00R | ROOF | ROOF | 11678 | SIPLAST PARADIENE 20/30 FR | 1997-08-01 | METAL | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -9 | 63100 | MAINTAIN | GOOD
225 | Toki | R04 | R04 | 00R | ROOF | TRACTOR STORAGE | 144 | SIPLAST PARADIENE 20/30 FR | 1997-08-01 | METAL | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -9 | 800 | MAINTAIN | GOOD
225 | Toki | R06 | R06 | 00R | ROOF | ROOF | 4812 | SIPLAST PARADIENE 20/30 FR | 2003-08-01 | METAL | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -3 | 26000 | MAINTAIN | GOOD
225 | Toki | R07 | R07 | 00R | ROOF | ROOF | 5165 | TARMAC SBS FR | 1992-08-01 | METAL | 34 | 5 | 3 | 3 | 3 | 5 | 3 | 3 | 56 | 20 | -14 | 27900 | REPLACE | POOR
225 | Toki | R08 | R08 | 00R | ROOF | ROOF | 488 | TARMAC SBS FR | 1992-08-01 | METAL | 34 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -14 | 2600 | REPAIR | FAIR
225 | Toki | R09 | R09 | 00R | ROOF | ROOF | 5042 | MANVILLE DYNAKAP FR | 1989-08-01 | METAL | 37 | 3 | 3 | 0 | 3 | 0 | 3 | 0 | 15 | 20 | -17 | 27200 | REPLACE | POOR
225 | Toki | R10 | R10 | 00R | ROOF | ROOF | 3279 | MANVILLE DYNAKAP FR | 1989-08-01 | METAL | 37 | 3 | 3 | 3 | 3 | 0 | 3 | 0 | 21 | 20 | -17 | 17700 | REPLACE | POOR
225 | Toki | R11 | R11 | 00R | ROOF | ROOF | 4935 | MANVILLE DYNAKAP FR | 1989-08-01 | METAL | 37 | 5 | 5 | 3 | 3 | 0 | 3 | 0 | 27 | 20 | -17 | 26600 | REPLACE | POOR
225 | Toki | R12 | R12 | 00R | ROOF | ROOF | 4388 | MANVILLE DYNAKAP FR | 1989-08-01 | METAL | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -17 | 23700 | MAINTAIN | GOOD
225 | Toki | R13 | R13 | 00R | ROOF | ROOF | 12781 | TARMAC SBS FR | 1992-08-01 | METAL | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14 | 69000 | MAINTAIN | GOOD
225 | Toki | R14 | R14 | 00R | ROOF | ROOF | 6452 | TARMAC SBS FR | 1992-08-01 | METAL | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14 | 34800 | MAINTAIN | GOOD
225 | Toki | R15 | R15 | 00R | ROOF | ROOF | 486 | SIPLAST PARADIENE 20/30 FR | 1997-08-01 | METAL | 29 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 5 | 20 | -9 | 2600 | REPAIR | FAIR
225 | Toki | R16 | R16 | 00R | ROOF | RELOCATABLE ROOF | 1611 | ASPHALT ROLLED ROOFING | 1962-08-01 | WOOD | 64 | 5 | 0 | 0 | 5 | 3 | 3 | 5 | 43 | 20 | -44 | 8700 | REPLACE | POOR
225 | Toki | R17 | R17 | 00R | ROOF | ROOF | 7182 | SIPLAST PARADIENE 20/30 FR | 1997-08-01 | METAL | 29 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 20 | -9 | 38800 | REPAIR | FAIR
225 | Toki | R18 | R18 | 00R | ROOF | ROOF | 12545 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | METAL | 24 | 3 | 5 | 3 | 3 | 0 | 0 | 0 | 20 | 20 | -4 | 67700 | REPLACE | POOR
225 | Toki | R19 | R19 | 00R | ROOF | ROOF | 9969 | SIPLAST PARADIENE 20/30 FR | 1999-08-01 | METAL | 27 | 0 | 5 | 3 | 0 | 0 | 3 | 0 | 14 | 20 | -7 | 53800 | REPAIR | FAIR
143 | West | R01 | R01 | 00R | ROOF | ROOF | 2805 | MANVILLE DYNAKAP FR | 1992-08-01 | ACOUSTICAL-METAL | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14 | 15100 | MAINTAIN | GOOD
143 | West | R02 | R02 | 00R | ROOF | ROOF | 17681 | MANVILLE DYNAKAP FR | 1992-08-01 | ACOUSTICAL-METAL | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14 | 95500 | MAINTAIN | GOOD
143 | West | R03 | R03 | 00R | ROOF | ROOF | 15985 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | UNKNOWN | 24 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -4 | 86300 | REPAIR | FAIR
143 | West | R04 | R04 | 00R | ROOF | ROOF | 9737 | SIPLAST PARADIENE 20/30 FR | 1986-08-01 | METAL | 40 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -20 | 52600 | REPAIR | POOR
143 | West | R05 | R05 | 00R | ROOF | ROOF | 988 | SIPLAST PARADIENE 20/30 FR | 1986-08-01 | METAL | 40 | 5 | 0 | 0 | 5 | 3 | 3 | 3 | 39 | 20 | -20 | 5300 | REPLACE | POOR
143 | West | R06 | R06 | 00R | ROOF | ROOF | 2521 | SIPLAST PARADIENE 20/30 FR | 2000-08-01 | METAL | 26 | 5 | 5 | 0 | 0 | 0 | 3 | 0 | 18 | 15 | -11 | 13600 | REPAIR | POOR
143 | West | R07 | R07 | 00R | ROOF | ROOF | 5712 | SIPLAST PARADIENE 20/30 FR | 1986-08-01 | METAL | 40 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -20 | 30800 | REPAIR | POOR
143 | West | R08 | R08 | 00R | ROOF | ROOF | 706 | SIPLAST PARADIENE 20/30 FR | 1986-08-01 | METAL | 40 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -20 | 3800 | REPAIR | POOR
143 | West | R09 | R09 | 00R | ROOF | ROOF | 13362 | SIPLAST PARADIENE 20/30 FR | 1993-08-01 | METAL | 33 | 0 | 0 | 0 | 0 | 1 | 3 | 3 | 14 | 20 | -13 | 72200 | REPAIR | FAIR
143 | West | R10 | R10 | 00R | ROOF | ROOF | 9759 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | UNKNOWN | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4 | 52700 | MAINTAIN | GOOD
143 | West | R11 | R11 | 00R | ROOF | ROOF | 2159 | CLAY TILE | 1984-08-01 | METAL | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 33 | 32400 | MAINTAIN | GOOD
143 | West | R12 | R12 | 00R | ROOF | ROOF | 1541 | SIPLAST PARADIENE 20/30 FR | 2000-08-01 | METAL | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | -11 | 8300 | MAINTAIN | GOOD
143 | West | R13 | R13 | 00R | ROOF | ROOF | 8063 | CLAY TILE | 1984-08-01 | METAL | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 33 | 120900 | MAINTAIN | GOOD
143 | West | R14 | R14 | 00R | ROOF | ROOF | 4837 | SIPLAST PARADIENE 20/30 FR | 2000-08-01 | METAL | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | -11 | 26100 | MAINTAIN | GOOD
143 | West | R15 | R15 | 00R | ROOF | ROOF | 1517 | SIPLAST PARADIENE 20/30 FR | 2000-08-01 | METAL | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | -11 | 8200 | MAINTAIN | GOOD
143 | West | R16 | R16 | 00R | ROOF | ROOF | 2219 | CLAY TILE | 1984-08-01 | METAL | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 33 | 33300 | MAINTAIN | GOOD
143 | West | R17 | R17 | 00R | ROOF | ROOF | 6878 | SIPLAST PARADIENE 20/30 FR | 2003-08-01 | UNKNOWN | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -3 | 37100 | MAINTAIN | GOOD
143 | West | R18 | R18 | 00R | ROOF | ROOF | 20592 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | UNKNOWN | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | -9 | 111200 | MAINTAIN | GOOD
143 | West | R19 | R19 | 00R | ROOF | ROOF | 6804 | MANVILLE DYNAKAP FR | 1990-08-01 | METAL | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -16 | 36700 | MAINTAIN | GOOD
143 | West | R20 | R20 | 00R | ROOF | ROOF | 1273 | BUR 4-PLY | 1965-08-01 | UNKNOWN | 61 | 5 | 0 | 0 | 5 | 3 | 3 | 5 | 43 | 20 | -41 | 6900 | REPLACE | POOR
143 | West | R21 | R21 | 00R | ROOF | ROOF | 597 | MANVILLE DYNAKAP FR | 1990-08-01 | METAL | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -16 | 3200 | MAINTAIN | GOOD
227 | Whitehorse | R01 | R01 | 00R | ROOF | ROOF | 15114 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4 | 81600 | MAINTAIN | GOOD
227 | Whitehorse | R02 | R02 | 00R | ROOF | ROOF | 2594 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4 | 14000 | MAINTAIN | GOOD
227 | Whitehorse | R03 | R03 | 00R | ROOF | ROOF | 11717 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4 | 63300 | MAINTAIN | GOOD
227 | Whitehorse | R04 | R04 | 00R | ROOF | ROOF | 4054 | TARMAC SBS FR | 1992-08-01 | METAL | 34 | 3 | 5 | 0 | 0 | 3 | 3 | 3 | 35 | 20 | -14 | 21900 | REPLACE | POOR
227 | Whitehorse | R05 | R05 | 00R | ROOF | ROOF | 5495 | TARMAC SBS FR | 1992-08-01 | METAL | 34 | 3 | 3 | 0 | 0 | 3 | 3 | 3 | 33 | 20 | -14 | 29700 | REPLACE | POOR
227 | Whitehorse | R06 | R06 | 00R | ROOF | ROOF | 4977 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4 | 26900 | MAINTAIN | GOOD
227 | Whitehorse | R07 | R07 | 00R | ROOF | ROOF | 1877 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4 | 10100 | MAINTAIN | GOOD
227 | Whitehorse | R08 | R08 | 00R | ROOF | ROOF | 208 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4 | 1100 | MAINTAIN | GOOD
227 | Whitehorse | R09 | R09 | 00R | ROOF | ROOF | 3746 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4 | 20200 | MAINTAIN | GOOD
227 | Whitehorse | R10 | R10 | 00R | ROOF | ROOF | 2006 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4 | 10800 | MAINTAIN | GOOD
227 | Whitehorse | R11 | R11 | 00R | ROOF | ROOF | 12955 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4 | 70000 | MAINTAIN | GOOD
227 | Whitehorse | R12 | R12 | 00R | ROOF | ROOF | 12966 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4 | 70000 | MAINTAIN | GOOD
227 | Whitehorse | R13 | R13 | 00R | ROOF | ROOF | 14315 | TAMKO VERSA CAP FR 2-PLY | 1995-08-01 | METAL | 31 | 3 | 5 | 3 | 3 | 3 | 3 | 3 | 44 | 20 | -11 | 77300 | REPLACE | POOR
227 | Whitehorse | R14 | R14 | 00R | ROOF | ROOF | 13183 | UNKNOWN | 1989-08-01 | METAL | 37 | 3 | 5 | 0 | 0 | 3 | 3 | 3 | 35 | 15 | -22 | 71200 | REPLACE | POOR
227 | Whitehorse | R15 | R15 | 00R | ROOF | ROOF | 4997 | TAMKO VERSA CAP FR 2-PLY | 1995-08-01 | METAL | 31 | 0 | 3 | 0 | 3 | 3 | 3 | 3 | 30 | 20 | -11 | 27000 | REPLACE | POOR
239 | Wright | C01 | C01 | 00R | ENTRANCE CANOPY | ROOF | 807 | SIPLAST PARADIENE 20/30 FR | 1997-08-01 | METAL | 29 | 0 | 3 | 0 | 0 | 3 | 3 | 3 | 27 | 20 | -9 | 4400 | REPAIR | FAIR
239 | Wright | R01 | R01 | 00R | ROOF | ROOF | 557 | SIPLAST PARADIENE 20/30 FR | 1997-08-01 | METAL | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -9 | 3000 | MAINTAIN | GOOD
239 | Wright | R02 | R02 | 00R | ROOF | ROOF | 16398 | SIPLAST PARADIENE 20/30 FR | 1997-08-01 | METAL | 29 | 0 | 3 | 2 | 0 | 3 | 3 | 3 | 31 | 20 | -9 | 88500 | REPLACE | POOR
239 | Wright | R03 | R03 | 00R | ROOF | ROOF | 2649 | SIPLAST PARADIENE 20/30 FR | 1997-08-01 | METAL | 29 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 20 | -9 | 14300 | REPAIR | FAIR
239 | Wright | R04 | R04 | 00R | ROOF | ROOF | 1596 | SIPLAST PARADIENE 20/30 FR | 1997-08-01 | METAL | 29 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 20 | -9 | 8600 | REPAIR | FAIR
239 | Wright | R05 | R05 | 00R | ROOF | ROOF | 10625 | SIPLAST PARADIENE 20/30 FR | 1997-08-01 | METAL | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -9 | 57400 | MAINTAIN | GOOD
239 | Wright | R06 | R06 | 00R | ROOF | ROOF | 1237 | SIPLAST PARADIENE 20/30 FR | 1997-08-01 | METAL | 29 | 0 | 0 | 0 | 0 | 3 | 1 | 3 | 22 | 20 | -9 | 6700 | REPAIR | FAIR
Totals: | [6 empty] | 2997673 | [14 empty] | 16674000
(1) Red indicates manual selection.
Formulas:
Date Installed = [Recommended Action, row above]_r!J2

## X004_r
Location Number | Location | Roof Identification Number | School Number | Level | Area Name | Roof Type | Area (Sq. Ft.) | Roof Type | Date Installed | Deck Information | Age (Years) | Drainage 0-Good Slope/No Ponding 3-Low Slope/Some Ponding 5-Poor Slope/Ponding | Blisters 0-No Blisters 3-Less Than 20 Percent 5-More Than 20 Percent | Linear Folds/Cracks 0-No Folds/Cracks 3-Less Than 20 Percent 5-More Than 20 Percent | Flashing Condition 0-Good 3-Some Splits/Cracks 5-Poor Splits/Cracks Common | Leakage Problems 0-No leaks 3-Minor Leaks 5-Major Leaks | Surface Wear 0-No Wear Noted 3-Average Wear Noted 5-Excessive Wear Noted | Deck 0-Concrete 3-Metal 5-Wood | Total Score Condition | Estimated Service Life | Estimated Remain Life
004 | Crestwood | R01 | R01 | 00R | GYM | ROOF | 3654 | GAF RUBEROID MB 131 MGPFR | 1993-06-03 | ACOUSTICAL-METAL | 33 | 0 | 5 | 3 | 3 | 0 | 3 | 0 | 17 | 20 | -13
004 | Crestwood | R02 | R02 | 00R | KITCHEN | ROOF | 507 | SIPLAST PARADIENE 20/30 FR | 2003-08-01 | METAL | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -3
004 | Crestwood | R03 | R03 | 00R | KITCHEN | ROOF | 702 | SIPLAST PARADIENE 20/30 FR | 2003-08-01 | METAL | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -3
004 | Crestwood | R04 | R04 | 00R | GYM | ROOF | 4735 | ARC | 1988-08-01 | METAL | 38 | 0 | 0 | 0 | 5 | 0 | 3 | 0 | 8 | 20 | -18
004 | Crestwood | R05 | R05 | 00R | LOCKER | ROOF | 1981 | SIPLAST PARADIENE 20/30 FR | 2003-08-01 | METAL | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -3
004 | Crestwood | R06 | R06 | 00R | ENTRANCE | ROOF | 724 | ARC | 1988-08-01 | METAL | 38 | 5 | 3 | 0 | 3 | 0 | 3 | 0 | 19 | 20 | -18
004 | Crestwood | R07 | R07 | 00R | ROOF | ROOF | 8715 | SIPLAST PARADIENE 20/30 FR | 2003-08-01 | WOOD | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -3
004 | Crestwood | R08 | R08 | 00R | ROOF | ROOF | 4600 | DERBIGUM-HPS | 1982-08-01 | METAL | 44 | 5 | 3 | 3 | 3 | 0 | 3 | 0 | 25 | 20 | -24
004 | Crestwood | R09 | R09 | 00R | ELEVATOR | ROOF | 540 | GAF RUBEROID MB 131 MGPFR | 1993-06-03 | METAL | 33 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | -13
004 | Crestwood | R10 | R10 | 00R | ROOF | ROOF | 7106 | BUR 4-PLY | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4
004 | Crestwood | R11 | R11 | 00R | LMC | ROOF | 2688 | GAF RUBEROID MB 131 MGPFR | 1993-06-03 | METAL | 33 | 3 | 5 | 3 | 3 | 3 | 3 | 3 | 44 | 20 | -13
004 | Crestwood | R12 | R12 | 00R | LMC | ROOF | 2980 | GAF RUBEROID MB 131 MGPFR | 1993-06-03 | METAL | 33 | 3 | 5 | 3 | 3 | 0 | 3 | 0 | 23 | 20 | -13
004 | Crestwood | R13 | R13 | 00R | BARREL-LMC | ROOF | 2688 | GAF RUBEROID MB 131 MGPFR | 1993-06-03 | WOOD | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -13
004 | Crestwood | R14 | R14 | 00R | LMC | ROOF | 121 | GAF RUBEROID MB 131 MGPFR | 1993-06-03 | METAL | 33 | 3 | 3 | 0 | 5 | 0 | 5 | 0 | 19 | 20 | -13
004 | Crestwood | R15 | R15 | 00R | LMC | ROOF | 485 | GAF RUBEROID MB 131 MGPFR | 1993-06-03 | METAL | 33 | 5 | 5 | 0 | 3 | 3 | 5 | 3 | 44 | 20 | -13
42226

## X301_r
Location Number | Location | Roof Identification Number | School Number | Level | Area Name | Roof Type | Area (Sq. Ft.) | Roof Type | Date Installed | Deck Information | Age (Years) | Drainage 0-Good Slope/No Ponding 3-Low Slope/Some Ponding 5-Poor Slope/Ponding | Blisters 0-No Blisters 3-Less Than 20 Percent 5-More Than 20 Percent | Linear Folds/Cracks 0-No Folds/Cracks 3-Less Than 20 Percent 5-More Than 20 Percent | Flashing Condition 0-Good 3-Some Splits/Cracks 5-Poor Splits/Cracks Common | Leakage Problems 0-No leaks 3-Minor Leaks 5-Major Leaks | Surface Wear 0-No Wear Noted 3-Average Wear Noted 5-Excessive Wear Noted | Deck 0-Concrete 3-Metal 5-Wood | Total Score Condition | Estimated Service Life | Estimated Remaining Life
301 | Administration | C01 | C01 | 00R | CANOPY | CANOPY | 162 | UNKNOWN | 1995-08-01 | UNKNOWN | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | -16
301 | Administration | C02 | C02 | 00R | CANOPY | CANOPY | 18 | UNKNOWN | 1995-08-01 | UNKNOWN | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | -16
301 | Administration | R01 | R01 | 00R | ROOF | ROOF | 3796 | MANVILLE DYNAGLAS FR | 1994-08-01 | CONCRETE | 32 | 3 | 3 | 0 | 2 | 0 | 3 | 0 | 14 | 20 | -12
301 | Administration | R02 | R02 | 00R | ROOF | ROOF | 68 | MANVILLE DYNAGLAS FR | 1994-08-01 | CONCRETE | 32 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -12
301 | Administration | R03 | R03 | 00R | ROOF | ROOF | 6985 | MANVILLE DYNAGLAS FR | 1994-08-01 | CONCRETE | 32 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -12
301 | Administration | R04 | R04 | 00R | ROOF | ROOF | 3314 | MANVILLE DYNAGLAS FR | 1994-08-01 | CONCRETE | 32 | 0 | 3 | 0 | 5 | 3 | 3 | 0 | 26 | 20 | -12
301 | Administration | R05 | R05 | 00R | ROOF | ROOF | 526 | MANVILLE DYNAGLAS FR | 1994-08-01 | CONCRETE | 32 | 3 | 3 | 0 | 5 | 0 | 3 | 0 | 17 | 20 | -12
301 | Administration | R06 | R06 | 00R | ROOF | ROOF | 5679 | MANVILLE DYNAGLAS FR | 1994-08-01 | CONCRETE | 32 | 0 | 5 | 5 | 5 | 0 | 3 | 0 | 23 | 20 | -12
301 | Administration | R07 | R07 | 00R | ROOF | ROOF | 603 | MANVILLE DYNAGLAS FR | 1994-08-01 | CONCRETE | 32 | 3 | 3 | 0 | 0 | 0 | 0 | 0 | 9 | 20 | -12
301 | Administration | R08 | R08 | 00R | ROOF | ROOF | 4194 | MANVILLE DYNAGLAS FR | 1994-08-01 | CONCRETE | 32 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -12
301 | Administration | R09 | R09 | 00R | ROOF | ROOF | 2418 | MANVILLE DYNAGLAS FR | 1994-08-01 | CONCRETE | 32 | 3 | 3 | 0 | 3 | 0 | 3 | 0 | 15 | 20 | -12
301 | Administration | R10 | R10 | 00R | ROOF | ROOF | 392 | MANVILLE DYNAGLAS FR | 1994-08-01 | CONCRETE | 32 | 3 | 5 | 0 | 3 | 0 | 3 | 0 | 17 | 20 | -12
301 | Administration | R11 | R11 | 00R | ROOF | ROOF | 171 | MANVILLE DYNAGLAS FR | 1994-08-01 | CONCRETE | 32 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -12
301 | Administration | R12 | R12 | 00R | ROOF | ROOF | 5436 | MANVILLE DYNAGLAS FR | 1994-08-01 | CONCRETE | 32 | 3 | 0 | 0 | 3 | 0 | 3 | 0 | 12 | 20 | -12
301 | Administration | R13 | R13 | 00R | ROOF | ROOF | 3369 | MANVILLE DYNAGLAS FR | 1994-08-01 | CONCRETE | 32 | 0 | 5 | 5 | 3 | 0 | 3 | 0 | 21 | 20 | -12
301 | Administration | R14 | R14 | 00R | ROOF | ROOF | 3196 | MANVILLE DYNAGLAS FR | 1994-08-01 | CONCRETE | 32 | 5 | 3 | 0 | 3 | 0 | 3 | 0 | 19 | 20 | -12
40327

## 305
Location Number | Location | Roof Identification Number | School Number | Level | Area Name | Roof Type | Area (Sq. Ft.) | Roof Type | Date Installed | Deck Information | Age (Years) | Drainage 0-Good Slope/No Ponding 3-Low Slope/Some Ponding 5-Poor Slope/Ponding | Blisters 0-No Blisters 3-Less Than 20 Percent 5-More Than 20 Percent | Linear Folds/Cracks 0-No Folds/Cracks 3-Less Than 20 Percent 5-More Than 20 Percent | Flashing Condition 0-Good 3-Some Splits/Cracks 5-Poor Splits/Cracks Common | Leakage Problems 0-No leaks 3-Minor Leaks 5-Major Leaks | Surface Wear 0-No Wear Noted 3-Average Wear Noted 5-Excessive Wear Noted | Deck 0-Concrete 3-Metal 5-Wood | Total Score Condition | Estimated Service Life | Estimated Remaining Life
305 | PFLAUM | C01 | C01 | 00R | MAIN ENTRANCE CANOPY | CANOPY | 60 | STANDING SEAM GALV/ALUM | 1987-08-01 | NONE | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | -14
305 | PFLAUM | C02 | C02 | 00R | CARPENTER CANOPY | CANOPY | 154 | STANDING SEAM GALV/ALUM | 1987-08-01 | NONE | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | -14
305 | PFLAUM | C03 | C03 | 00R | MAINTENANCE CANOPY | CANOPY | 154 | STANDING SEAM GALV/ALUM | 1987-08-01 | NONE | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | -14
305 | PFLAUM | C04 | C04 | 00R | PAINT CANOPY | CANOPY | 169 | STANDING SEAM GALV/ALUM | 1987-08-01 | NONE | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | -14
305 | PFLAUM | C05 | C05 | 00R | SM. ENGINE CANOPY | CANOPY | 95 | STANDING SEAM GALV/ALUM | 1987-08-01 | NONE | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | -14
305 | PFLAUM | R01 | R01 | 00R | ROOF | ROOF | 50067 | STANDING SEAM GALV/ALUM | 1987-08-01 | METAL/SKYLIGHTS | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | -14
305 | PFLAUM | R02 | R02 | 00R | LOADING DOCK ROOF | ROOF | 2622 | METAL | 1991-08-01 | NONE | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | -10
305 | PFLAUM | R03 | R03 | 00R | FPC UPPER ROOF | ROOF | 12355 | METAL | 1991-08-01 | NONE | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | -10
305 | PFLAUM | R04 | R04 | 00R | FPC LOWER ROOF | ROOF | 4202 | METAL | 1991-08-01 | NONE | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | -10
69878

## X006_r
Location Number | Location | Roof Identification Number | School Number | Level | Area Name | Roof Type | Area (Sq. Ft.) | Roof Type | Date Installed | Deck Information | Age (Years) | Drainage 0-Good Slope/No Ponding 3-Low Slope/Some Ponding 5-Poor Slope/Ponding | Blisters 0-No Blisters 3-Less Than 20 Percent 5-More Than 20 Percent | Linear Folds/Cracks 0-No Folds/Cracks 3-Less Than 20 Percent 5-More Than 20 Percent | Flashing Condition 0-Good 3-Some Splits/Cracks 5-Poor Splits/Cracks Common | Leakage Problems 0-No leaks 3-Minor Leaks 5-Major Leaks | Surface Wear 0-No Wear Noted 3-Average Wear Noted 5-Excessive Wear Noted | Deck 0-Concrete 3-Metal 5-Wood | Total Score Condition | Estimated Service Life | Estimated Remaining Life
006 | Elvejhem | R01 | R01 | 00R | ROOF | ROOF | 13630 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | WOOD | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4
006 | Elvejhem | R02 | R02 | 00R | CAFETERIA | ROOF | 4348 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | WOOD | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4
006 | Elvejhem | R03 | R03 | 00R | ROOF | ROOF | 26444 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | WOOD | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4
006 | Elvejhem | R04 | R04 | 00R | ROOF | ROOF | 10552 | GAF GAFGLAS 104G | 1993-12-31 | WOOD | 33 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 6 | 20 | -13
006 | Elvejhem | R05 | R05 | 00R | GYM | ROOF | 5418 | GAF GAFGLAS 104G | 1993-12-31 | ACOUSTICAL-METAL | 33 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -13
006 | Elvejhem | R06 | R06 | 00R | ROOF | ROOF | 10552 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | WOOD | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4
70944

## X008_r
Location Number | Location | Roof Identification Number | School Number | Level | Area Name | Roof Type | Area (Sq. Ft.) | Roof Type | Date Installed | Deck Information | Age (Years) | Drainage 0-Good Slope/No Ponding 3-Low Slope/Some Ponding 5-Poor Slope/Ponding | Blisters 0-No Blisters 3-Less Than 20 Percent 5-More Than 20 Percent | Linear Folds/Cracks 0-No Folds/Cracks 3-Less Than 20 Percent 5-More Than 20 Percent | Flashing Condition 0-Good 3-Some Splits/Cracks 5-Poor Splits/Cracks Common | Leakage Problems 0-No leaks 3-Minor Leaks 5-Major Leaks | Surface Wear 0-No Wear Noted 3-Average Wear Noted 5-Excessive Wear Noted | Deck 0-Concrete 3-Metal 5-Wood | Total Score Condition | Estimated Service Life | Estimated Remaining Life
008 | Franklin | R01 | R01 | 00R | ROOF | ROOF | 2133 | UNKNOWN | 1965-08-01 | UNKNOWN | 61 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 15 | -46
008 | Franklin | R02 | R02 | 00R | ROOF | ROOF | 3019 | GEOFLEX-PIB | 1982-08-01 | WOOD | 44 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -24
008 | Franklin | R03 | R03 | 00R | ROOF | ROOF | 3033 | UNKNOWN | 1965-08-01 | UNKNOWN | 61 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 15 | -46
008 | Franklin | R04 | R04 | 00R | ROOF | ROOF | 2949 | MANVILLE DYNAGLAS FR | 1991-08-01 | CONCRETE | 35 | 3 | 3 | 0 | 3 | 0 | 3 | 0 | 15 | 20 | -15
008 | Franklin | R05 | R05 | 00R | ROOF | ROOF | 4336 | MANVILLE DYNAGLAS FR | 1991-08-01 | METAL | 35 | 3 | 3 | 3 | 3 | 0 | 3 | 0 | 21 | 20 | -15
008 | Franklin | R06 | R06 | 00R | ROOF | ROOF | 2340 | SIPLAST PARADIENE 20/30 FR | 1985-08-01 | METAL | 41 | 0 | 0 | 0 | 3 | 3 | 3 | 3 | 27 | 20 | -21
008 | Franklin | R07 | R07 | 00R | ROOF | ROOF | 149 | GEOFLEX-PIB | 1982-08-01 | WOOD | 44 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 8 | 20 | -24
008 | Franklin | R08 | R08 | 00R | ROOF | ROOF | 137 | UNKNOWN | 1965-08-01 | UNKNOWN | 61 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 8 | 15 | -46
008 | Franklin | R09 | R09 | 00R | ROOF | ROOF | 225 | UNKNOWN | 1965-08-01 | UNKNOWN | 61 | 3 | 0 | 0 | 3 | 3 | 3 | 5 | 37 | 15 | -46
008 | Franklin | R10 | R10 | 00R | ROOF | ROOF | 95 | COPPER | 1965-08-01 | UNKNOWN | 61 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 6 | 25 | -36
008 | Franklin | R11 | R11 | 00R | ROOF | ELECTRICAL | 229 | EPDM BALLAST | 1995-08-01 | WOOD | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | -16
18645

## X016_r
Location Number | Location | Roof Identification Number | School Number | Level | Area Name | Roof Type | Area (Sq. Ft.) | Roof Type | Date Installed | Deck Information | Age (Years) | Drainage 0-Good Slope/No Ponding 3-Low Slope/Some Ponding 5-Poor Slope/Ponding | Blisters 0-No Blisters 3-Less Than 20 Percent 5-More Than 20 Percent | Linear Folds/Cracks 0-No Folds/Cracks 3-Less Than 20 Percent 5-More Than 20 Percent | Flashing Condition 0-Good 3-Some Splits/Cracks 5-Poor Splits/Cracks Common | Leakage Problems 0-No leaks 3-Minor Leaks 5-Major Leaks | Surface Wear 0-No Wear Noted 3-Average Wear Noted 5-Excessive Wear Noted | Deck 0-Concrete 3-Metal 5-Wood | Total Score Age + Condition | Estimated Service Life | Estimated Remaining Life
016 | Lapham | R01 | R01 | 00R | POOL | ROOF | 4792 | SIPLAST PARADIENE 20/30 FR | 2003-08-01 | CONCRETE | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -3
016 | Lapham | R02 | R02 | 00R | ROOF | ROOF | 7213 | SIPLAST PARADIENE 20/30 FR | 1984-08-01 | CONCRETE | 42 | 3 | 3 | 0 | 3 | 0 | 5 | 0 | 17 | 20 | -22
016 | Lapham | R03 | R03 | 00R | ROOF | ROOF | 4207 | SIPLAST PARADIENE 20/30 FR | 1988-08-01 | CONCRETE | 38 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | -18
016 | Lapham | R04 | R04 | 00R | CANOPY | CANOPY | 1128 | UNKNOWN | 1965-08-01 | UNKNOWN | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | -46
016 | Lapham | R05 | R05 | 00R | ROOF | ROOF | 2957 | SIPLAST PARADIENE 20/30 FR | 1988-08-01 | CONCRETE | 38 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | -18
016 | Lapham | R06 | R06 | 00R | ROOF | ROOF | 1061 | SIPLAST PARADIENE 20/30 FR | 1988-08-01 | CONCRETE | 38 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -18
016 | Lapham | R07 | R07 | 00R | ROOF | ROOF | 5570 | SIPLAST PARADIENE 20/30 FR | 1988-08-01 | CONCRETE | 38 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | -18
016 | Lapham | R08 | R08 | 00R | ROOF | ROOF | 5555 | SIPLAST PARADIENE 20/30 FR | 1988-08-01 | CONCRETE | 38 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -18
016 | Lapham | R09 | R09 | 00R | ROOF | ROOF | 2780 | SIPLAST PARADIENE 20/30 FR | 1988-08-01 | CONCRETE | 38 | 3 | 3 | 0 | 0 | 0 | 3 | 0 | 12 | 20 | -18
35263

## X009_r
Location Number | Location | Roof Identification Number | School Number | Level | Area Name | Roof Type | Area (Sq. Ft.) | Roof Type | Date Installed | Deck Information | Age (Years) | Drainage 0-Good Slope/No Ponding 3-Low Slope/Some Ponding 5-Poor Slope/Ponding | Blisters 0-No Blisters 3-Less Than 20 Percent 5-More Than 20 Percent | Linear Folds/Cracks 0-No Folds/Cracks 3-Less Than 20 Percent 5-More Than 20 Percent | Flashing Condition 0-Good 3-Some Splits/Cracks 5-Poor Splits/Cracks Common | Leakage Problems 0-No leaks 3-Minor Leaks 5-Major Leaks | Surface Wear 0-No Wear Noted 3-Average Wear Noted 5-Excessive Wear Noted | Deck 0-Concrete 3-Metal 5-Wood | Total Score Condition | Estimated Service Life | Estimated Remaining Life
009 | Glendale | R01 | R01 | 00R | R00F | ROOF | 13675 | FIRESTONE EPDM W/BALLAST | 1989-08-01 | METAL | 37 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 15 | -22
009 | Glendale | R02 | R02 | 00R | CANOPY | ROOF | 257 | SIPLAST PARADIENE 20/30 FR TG | 2003-08-01 | METAL | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -3
009 | Glendale | R03 | R03 | 00R | LMC-GYM-ROOF | ROOF | 7101 | SIPLAST PARADIENE 20/30 FR TG | 2003-08-01 | METAL | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -3
009 | Glendale | R04 | R04 | 00R | CANOPY | ROOF | 182 | SIPLAST PARADIENE 20/30 FR TG | 2003-08-01 | METAL | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -3
009 | Glendale | R05 | R05 | 00R | CANOPY | ROOF | 277 | SIPLAST PARADIENE 20/30 FR TG | 2003-08-01 | METAL | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -3
009 | Glendale | R06 | R06 | 00R | R00F | ROOF | 11236 | FIRESTONE EPDM W/BALLAST | 1989-08-01 | METAL | 37 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 15 | -22
009 | Glendale | R07 | R07 | 00R | R00F | ROOF | 11389 | FIRESTONE EPDM W/BALLAST | 1989-08-01 | METAL | 37 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 15 | -22
44117

## 011_r
Location Number | Location | Roof Identification Number | School Number | Level | Area Name | Roof Type | Area (Sq. Ft.) | Roof Type | Date Installed | Deck Information | Age (Years) | Drainage 0-Good Slope/No Ponding 3-Low Slope/Some Ponding 5-Poor Slope/Ponding | Blisters 0-No Blisters 3-Less Than 20 Percent 5-More Than 20 Percent | Linear Folds/Cracks 0-No Folds/Cracks 3-Less Than 20 Percent 5-More Than 20 Percent | Flashing Condition 0-Good 3-Some Splits/Cracks 5-Poor Splits/Cracks Common | Leakage Problems 0-No leaks 3-Minor Leaks 5-Major Leaks | Surface Wear 0-No Wear Noted 3-Average Wear Noted 5-Excessive Wear Noted | Deck 0-Concrete 3-Metal 5-Wood | Total Score Condition | Estimated Service Life | Estimated Remaining Life
011 | Falk | R01 | R01 | 00R | ROOF | ROOF | 14687 | BUR W/ PEA GRAVEL | 1995-08-01 | METAL | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -11
011 | Falk | R02 | R02 | 00R | ROOF | ROOF | 19145 | BUR W/ PEA GRAVEL | 1995-08-01 | WOOD | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -11
011 | Falk | R03 | R03 | 00R | LMC | ROOF | 5946 | BUR W/ PEA GRAVEL | 1995-08-01 | UNKNOWN | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -11
011 | Falk | R04 | R04 | 00R | ROOF | ROOF | 14270 | BUR W/ PEA GRAVEL | 1995-08-01 | WOOD | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -11
011 | Falk | R05 | R05 | 00R | ROOF | ROOF | 5417 | BUR W/ PEA GRAVEL | 1995-08-01 | UNKNOWN | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -11
011 | Falk | R06 | R06 | 00R | MUSIC | ROOF | 945 | BUR W/ PEA GRAVEL | 1995-08-01 | METAL | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -11
011 | Falk | R07 | R07 | 00R | GYM | ROOF | 9858 | BUR W/ PEA GRAVEL | 1995-08-01 | METAL | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -11
011 | Falk | R08 | R08 | 00R | ROOF | ROOF | 1750 | BUR W/ PEA GRAVEL | 1995-08-01 | METAL | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -11
72018

## X012_R
Location Number | Location | Roof Identification Number | School Number | Level | Area Name | Roof Type | Area (Sq. Ft.) | Roof Type | Date Installed | Deck Information | Age (Years) | Drainage 0-Good Slope/No Ponding 3-Low Slope/Some Ponding 5-Poor Slope/Ponding | Blisters 0-No Blisters 3-Less Than 20 Percent 5-More Than 20 Percent | Linear Folds/Cracks 0-No Folds/Cracks 3-Less Than 20 Percent 5-More Than 20 Percent | Flashing Condition 0-Good 3-Some Splits/Cracks 5-Poor Splits/Cracks Common | Leakage Problems 0-No leaks 3-Minor Leaks 5-Major Leaks | Surface Wear 0-No Wear Noted 3-Average Wear Noted 5-Excessive Wear Noted | Deck 0-Concrete 3-Metal 5-Wood | Total Score Condition | Estimated Service Life | Estimated Remaining Life
012 | Hawthorne | R01 | R01 | 00R | ROOF | ROOF | 5624 | BUR W/ PEA GRAVEL | 1987-08-01 | METAL | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -19
012 | Hawthorne | R02 | R02 | 00R | ROOF | ROOF | 22443 | BUR W/ PEA GRAVEL | 1987-08-01 | METAL | 39 | 0 | 1 | 0 | 3 | 0 | 0 | 0 | 4 | 20 | -19
012 | Hawthorne | R03 | R03 | 00R | LOCKER | ROOF | 1940 | BUR W/ PEA GRAVEL | 1987-08-01 | METAL | 39 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 3 | 20 | -19
012 | Hawthorne | R04 | R04 | 00R | GYM | ROOF | 4833 | BUR W/ PEA GRAVEL | 1987-08-01 | FINESTRA | 39 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -19
012 | Hawthorne | R05 | R05 | 00R | LMC | ROOF | 5866 | BUR W/ PEA GRAVEL | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5
012 | Hawthorne | R06 | R06 | 00R | ROOF | ROOF | 1231 | BUR W/ PEA GRAVEL | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5
41937

## X013_R
Location Number | Location | Roof Identification Number | School Number | Level | Area Name | Roof Type | Area (Sq. Ft.) | Roof Type | Date Installed | Deck Information | Age (Years) | Drainage 0-Good Slope/No Ponding 3-Low Slope/Some Ponding 5-Poor Slope/Ponding | Blisters 0-No Blisters 3-Less Than 20 Percent 5-More Than 20 Percent | Linear Folds/Cracks 0-No Folds/Cracks 3-Less Than 20 Percent 5-More Than 20 Percent | Flashing Condition 0-Good 3-Some Splits/Cracks 5-Poor Splits/Cracks Common | Leakage Problems 0-No leaks 3-Minor Leaks 5-Major Leaks | Surface Wear 0-No Wear Noted 3-Average Wear Noted 5-Excessive Wear Noted | Deck 0-Concrete 3-Metal 5-Wood | Total Score Condition | Estimated Service Life | Estimated Remaining Life
013 | Hoyt | R01 | R01 | 00R | ROOF | ROOF | 12818 | BUR W/ PEA GRAVEL | 1988-08-01 | UNKNOWN | 38 | 0 | 0 | 0 | 3 | 1 | 0 | 5 | 18 | 20 | -18
013 | Hoyt | R02 | R02 | 00R | ROOF | ROOF | 6645 | BUR W/ PEA GRAVEL | 1988-08-01 | UNKNOWN | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -18
013 | Hoyt | R03 | R03 | 00R | ROOF | ROOF | 5844 | BUR W/ PEA GRAVEL | 1988-08-01 | UNKNOWN | 38 | 0 | 0 | 0 | 3 | 1 | 0 | 5 | 18 | 20 | -18
013 | Hoyt | R04 | R04 | 00R | GYM | ROOF | 4241 | BUR W/ PEA GRAVEL | 1988-08-01 | UNKNOWN | 38 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 3 | 20 | -18
29548

## 014_r
Location Number | Location | Roof Identification Number | School Number | Level | Area Name | Roof Type | Area (Sq. Ft.) | Roof Type | Date Installed | Deck Information | Age (Years) | Drainage 0-Good Slope/No Ponding 3-Low Slope/Some Ponding 5-Poor Slope/Ponding | Blisters 0-No Blisters 3-Less Than 20 Percent 5-More Than 20 Percent | Linear Folds/Cracks 0-No Folds/Cracks 3-Less Than 20 Percent 5-More Than 20 Percent | Flashing Condition 0-Good 3-Some Splits/Cracks 5-Poor Splits/Cracks Common | Leakage Problems 0-No leaks 3-Minor Leaks 5-Major Leaks | Surface Wear 0-No Wear Noted 3-Average Wear Noted 5-Excessive Wear Noted | Deck 0-Concrete 3-Metal 5-Wood | Total Score Condition | Estimated Service Life | Estimated Remaining Life
014 | Lakeview | C01 | C01 | 00R | ENTRANCE-CANOPY | CANOPY | 924 | BUR W/ PEA GRAVEL | 1991-08-01 | WOOD | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -15
014 | Lakeview | C02 | C02 | 00R | RECEIVING-CANOPY | CANOPY | 546 | BUR W/ PEA GRAVEL | 1991-08-01 | WOOD | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -15
014 | Lakeview | C03 | C03 | 00R | CANOPY | CANOPY | 276 | BUR W/ PEA GRAVEL | 1991-08-01 | WOOD | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -15
014 | Lakeview | R01 | R01 | 00R | LOCKER | ROOF | 2071 | BUR W/ PEA GRAVEL | 1991-08-01 | WOOD | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -15
014 | Lakeview | R02 | R02 | 00R | GYM | ROOF | 4471 | BUR W/ PEA GRAVEL | 1991-08-01 | WOOD | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -15
014 | Lakeview | R03 | R03 | 00R | ROOF | ROOF | 7961 | BUR W/ PEA GRAVEL | 1991-08-01 | WOOD | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -15
014 | Lakeview | R04 | R04 | 00R | ROOF | ROOF | 6697 | BUR W/ PEA GRAVEL | 1991-08-01 | WOOD | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -15
014 | Lakeview | R05 | R05 | 00R | ROOF | ROOF | 6155 | BUR W/ PEA GRAVEL | 1991-08-01 | WOOD | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -15
29101

## X017_R
Location Number | Location | Roof Identification Number | School Number | Level | Area Name | Roof Type | Area (Sq. Ft.) | Roof Type | Date Installed | Deck Information | Age (Years) | Drainage 0-Good Slope/No Ponding 3-Low Slope/Some Ponding 5-Poor Slope/Ponding | Blisters 0-No Blisters 3-Less Than 20 Percent 5-More Than 20 Percent | Linear Folds/Cracks 0-No Folds/Cracks 3-Less Than 20 Percent 5-More Than 20 Percent | Flashing Condition 0-Good 3-Some Splits/Cracks 5-Poor Splits/Cracks Common | Leakage Problems 0-No leaks 3-Minor Leaks 5-Major Leaks | Surface Wear 0-No Wear Noted 3-Average Wear Noted 5-Excessive Wear Noted | Deck 0-Concrete 3-Metal 5-Wood | Total Score Condition | Estimated Service Life | Estimated Remaining Life
017 | Muir | C01 | C01 | 00R | CANOPY | CANOPY | 116 | MANVILLE 4-PLY BUR | 1992-08-01 | METAL | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14
017 | Muir | C02 | C02 | 00R | CANOPY | CANOPY | 119 | MANVILLE 4-PLY BUR | 1992-08-01 | METAL | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14
017 | Muir | R01 | R01 | 00R | ROOF | ROOF | 5056 | MANVILLE 4-PLY BUR | 1992-08-01 | METAL | 34 | 0 | 0 | 0 | 1 | 0 | 3 | 0 | 4 | 20 | -14
017 | Muir | R02 | R02 | 00R | ROOF | ROOF | 709 | MANVILLE 4-PLY BUR | 1992-08-01 | METAL | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14
017 | Muir | R03 | R03 | 00R | ROOF | ROOF | 645 | MANVILLE 4-PLY BUR | 1992-08-01 | METAL | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14
017 | Muir | R04 | R04 | 00R | ROOF | ROOF | 4603 | MANVILLE 4-PLY BUR | 1992-08-01 | METAL | 34 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 3 | 20 | -14
017 | Muir | R05 | R05 | 00R | ROOF | ROOF | 269 | MANVILLE 4-PLY BUR | 1992-08-01 | METAL | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14
017 | Muir | R06 | R06 | 00R | ROOF | ROOF | 1627 | SIPLAST PARADIENE 20/30 FR | 1998-08-01 | CONCRETE | 28 | 3 | 0 | 0 | 0 | 0 | 4 | 0 | 10 | 20 | -8
017 | Muir | R07 | R07 | 00R | ROOF | ROOF | 719 | MANVILLE 4-PLY BUR | 1992-08-01 | METAL | 34 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 3 | 20 | -14
017 | Muir | R08 | R08 | 00R | ROOF | ROOF | 627 | MANVILLE 4-PLY BUR | 1992-08-01 | METAL | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14
017 | Muir | R09 | R09 | 00R | ROOF | ROOF | 5107 | MANVILLE 4-PLY BUR | 1992-08-01 | METAL | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14
017 | Muir | R10 | R10 | 00R | ROOF | ROOF | 4555 | SIPLAST PARADIENE 20/30 FR | 1988-08-01 | WOOD FIBER | 38 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 20 | -18
017 | Muir | R11 | R11 | 00R | ROOF | ROOF | 13903 | SIPLAST PARADIENE 20/30 FR | 1988-08-01 | METAL | 38 | 3 | 3 | 0 | 0 | 0 | 0 | 0 | 9 | 20 | -18
017 | Muir | R12 | R12 | 00R | ROOF | ROOF | 13913 | SIPLAST PARADIENE 20/30 FR | 1988-08-01 | METAL | 38 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -18
017 | Muir | R13 | R13 | 00R | ROOF | ROOF | 3932 | MANVILLE 4-PLY BUR | 1992-08-01 | METAL | 34 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -14
017 | Muir | R14 | R14 | 00R | ROOF | ROOF | 5682 | SIPLAST PARADIENE 20/30 FR | 1988-08-01 | METAL | 38 | 0 | 1 | 0 | 0 | 0 | 3 | 0 | 4 | 20 | -18
017 | Muir | R15 | R15 | 00R | ROOF | ROOF | 315 | UNKNOWN | 1989-08-01 | METAL | 37 | 0 | 5 | 1 | 0 | 0 | 3 | 0 | 10 | 15 | -22
017 | Muir | R16 | R16 | 00R | 1ST ADDITION ROOF | ROOF | 5323 | UNKNOWN | 1989-08-01 | METAL | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | -22
67220

## X019_R
Location Number | Location | Roof Identification Number | School Number | Level | Area Name | Roof Type | Area (Sq. Ft.) | Roof Type | Date Installed | Deck Information | Age (Years) | Drainage 0-Good Slope/No Ponding 3-Low Slope/Some Ponding 5-Poor Slope/Ponding | Blisters 0-No Blisters 3-Less Than 20 Percent 5-More Than 20 Percent | Linear Folds/Cracks 0-No Folds/Cracks 3-Less Than 20 Percent 5-More Than 20 Percent | Flashing Condition 0-Good 3-Some Splits/Cracks 5-Poor Splits/Cracks Common | Leakage Problems 0-No leaks 3-Minor Leaks 5-Major Leaks | Surface Wear 0-No Wear Noted 3-Average Wear Noted 5-Excessive Wear Noted | Deck 0-Concrete 3-Metal 5-Wood | Total Score Condition | Estimated Service Life | Estimated Remaining Life
019 | Lowell | C01 | C01 | 00R | MAPLE ST. ENTRANCE CANOPY | CANOPY | 0 | REMOVED | 2003-08-01 | UNKNOWN | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -23
019 | Lowell | R01 | R01 | 00R | ROOF | ROOF | 795 | SIPLAST PARADIENE 20/30 FR | 1985-08-01 | WOOD | 41 | 0 | 3 | 2 | 0 | 0 | 3 | 0 | 10 | 20 | -21
019 | Lowell | R02 | R02 | 00R | ROOF | ROOF | 1678 | SIPLAST PARADIENE 20/30 FR | 1985-08-01 | WOOD | 41 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -21
019 | Lowell | R03 | R03 | 00R | ROOF | ROOF | 2934 | SIPLAST PARADIENE 20/30 FR | 1985-08-01 | WOOD | 41 | 0 | 3 | 3 | 0 | 0 | 3 | 0 | 12 | 20 | -21
019 | Lowell | R04 | R04 | 00R | ROOF | ROOF | 567 | SIPLAST PARADIENE 20/30 FR | 1985-08-01 | WOOD | 41 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -21
019 | Lowell | R05 | R05 | 00R | ROOF | ROOF | 799 | SIPLAST PARADIENE 20/30 FR | 1985-08-01 | WOOD | 41 | 0 | 3 | 3 | 0 | 0 | 3 | 0 | 12 | 20 | -21
019 | Lowell | R06 | R06 | 00R | ROOF | ROOF | 1707 | SIPLAST PARADIENE 20/30 FR | 1985-08-01 | WOOD | 41 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -21
019 | Lowell | R07 | R07 | 00R | ROOF | ROOF | 726 | CLAY TILE WITH FELT BELOW | 1995-08-01 | WOOD | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 44
019 | Lowell | R08 | R08 | 00R | ROOF | ROOF | 79 | CLAY TILE | 1927-08-01 | WOOD | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | -24
019 | Lowell | R08A | R08A | 00R | ROOF | ROOF | 251 | CLAY TILE | 1927-08-01 | WOOD | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | -24
019 | Lowell | R09 | R09 | 00R | ROOF | ROOF | 233 | CLAY TILE | 1927-08-01 | WOOD | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | -24
019 | Lowell | R10 | R10 | 00R | ROOF | ROOF | 250 | CLAY TILE | 1927-08-01 | WOOD | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | -24
019 | Lowell | R11 | R11 | 00R | ROOF | ROOF | 246 | CLAY TILE | 1927-08-01 | WOOD | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | -24
019 | Lowell | R12 | R12 | 00R | ROOF | ROOF | 14560 | SIPLAST PARADIENE 20/30 FR | 1985-08-01 | CONCRETE | 41 | 3 | 3 | 0 | 0 | 0 | 3 | 0 | 12 | 20 | -21
019 | Lowell | R13 | R13 | 00R | ROOF | ROOF | 1433 | SIPLAST PARADIENE 20/30 FR | 1985-08-01 | CONCRETE | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -21
019 | Lowell | R14 | R14 | 00R | ROOF | ROOF | 1071 | SIPLAST PARADIENE 20/30 FR | 1985-08-01 | CONCRETE | 41 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -21
019 | Lowell | R15 | R15 | 00R | ROOF | ROOF | 4018 | EPDM/LG BOARD | 1985-08-01 | CONCRETE | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | -26
019 | Lowell | R16 | R16 | 00R | STAIR ROOF | ROOF | 441 | CONCRETE TILE | 1985-08-01 | CONCRETE | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -21
019 | Lowell | R17 | R17 | 00R | TRACTOR STORAGE ROOF | ROOF | 139 | UNKNOWN | 1991-08-01 | UNKNOWN | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | -20

## X021_r
Location Number | Location | Roof Identification Number | School Number | Level | Area Name | Roof Type | Area (Sq. Ft.) | Roof Type | Date Installed | Deck Information | Age (Years) | Drainage 0-Good Slope/No Ponding 3-Low Slope/Some Ponding 5-Poor Slope/Ponding | Blisters 0-No Blisters 3-Less Than 20 Percent 5-More Than 20 Percent | Linear Folds/Cracks 0-No Folds/Cracks 3-Less Than 20 Percent 5-More Than 20 Percent | Flashing Condition 0-Good 3-Some Splits/Cracks 5-Poor Splits/Cracks Common | Leakage Problems 0-No leaks 3-Minor Leaks 5-Major Leaks | Surface Wear 0-No Wear Noted 3-Average Wear Noted 5-Excessive Wear Noted | Deck 0-Concrete 3-Metal 5-Wood | Total Score Condition | Estimated Service Life | Estimated Remaining Life
021 | Mendota | C01 | C01 | 00R | CANOPY | CANOPY | 63 | TARMAC SBS FR | 1991-08-01 | WOOD-METAL | 35 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 6 | 20 | -15
021 | Mendota | R01 | R01 | 00R | ROOF | ROOF | 5206 | SIPLAST PARADIENE 20/30 FR | 2003-08-01 | METAL | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -3
021 | Mendota | R02 | R02 | 00R | ROOF | ROOF | 582 | MANVILLE DYNAKAP FR | 1987-08-01 | CONCRETE | 39 | 5 | 0 | 5 | 3 | 0 | 5 | 0 | 28 | 20 | -19
021 | Mendota | R03 | R03 | 00R | ROOF | ROOF | 4545 | MANVILLE DYNAKAP FR | 1987-08-01 | WOOD | 39 | 5 | 3 | 5 | 3 | 3 | 5 | 5 | 56 | 20 | -19
021 | Mendota | R04 | R04 | 00R | ROOF | ROOF | 9829 | MANVILLE DYNAKAP FR | 1987-08-01 | WOOD | 39 | 3 | 3 | 5 | 3 | 3 | 5 | 5 | 52 | 20 | -19
021 | Mendota | R05 | R05 | 00R | ROOF | ROOF | 6639 | MANVILLE DYNAKAP FR | 1987-08-01 | WOOD | 39 | 5 | 3 | 5 | 3 | 0 | 5 | 0 | 31 | 20 | -19
021 | Mendota | R06 | R06 | 00R | GYM ROOF | ROOF | 3454 | SIPLAST PARADIENE 20/30 FR TG | 2003-08-01 | METAL | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -3
021 | Mendota | R07 | R07 | 00R | ROOF | ROOF | 1282 | MANVILLE DYNAKAP FR | 1987-08-01 | WOOD | 39 | 5 | 0 | 0 | 3 | 0 | 5 | 0 | 18 | 20 | -19
021 | Mendota | R08 | R08 | 00R | ROOF | ROOF | 12114 | TARMAC SBS FR | 1991-08-01 | WOOD-METAL | 35 | 3 | 5 | 0 | 5 | 0 | 3 | 0 | 19 | 20 | -15
021 | Mendota | R09 | R09 | 00R | ROOF | ROOF | 2084 | TARMAC SBS FR | 1991-08-01 | WOOD-METAL | 35 | 3 | 3 | 0 | 3 | 0 | 3 | 0 | 15 | 20 | -15
45798

## X022_R
Location Number | Location | Roof Identification Number | School Number | Level | Area Name | Roof Type | Area (Sq. Ft.) | Roof Type | Date Installed | Deck Information | Age (Years) | Drainage 0-Good Slope/No Ponding 3-Low Slope/Some Ponding 5-Poor Slope/Ponding | Blisters 0-No Blisters 3-Less Than 20 Percent 5-More Than 20 Percent | Linear Folds/Cracks 0-No Folds/Cracks 3-Less Than 20 Percent 5-More Than 20 Percent | Flashing Condition 0-Good 3-Some Splits/Cracks 5-Poor Splits/Cracks Common | Leakage Problems 0-No leaks 3-Minor Leaks 5-Major Leaks | Surface Wear 0-No Wear Noted 3-Average Wear Noted 5-Excessive Wear Noted | Deck 0-Concrete 3-Metal 5-Wood | Total Score Condition | Estimated Service Life | Estimated Remaining Life
022 | Midvale | R01 | R01 | 00R | GYM ROOF | ROOF | 7634 | CELOTEX-CELOPAL-I | 1985-08-01 | GYPSUM | 41 | 0 | 3 | 3 | 0 | 0 | 3 | 0 | 12 | 20 | -21
022 | Midvale | R02 | R02 | 00R | ROOF | ROOF | 8593 | SIPLAST PARADIENE 20/30 FR | 1981-08-01 | UNKNOWN | 45 | 3 | 5 | 3 | 3 | 0 | 3 | 0 | 23 | 20 | -25
022 | Midvale | R03 | R03 | 00R | ROOF | ROOF | 9763 | CELOTEX CP101C | 1986-08-01 | UNKNOWN | 40 | 5 | 5 | 3 | 3 | 2 | 5 | 5 | 49 | 20 | -20
25990

## X023_R
Location Number | Location | Roof Identification Number | School Number | Level | Area Name | Roof Type | Area (Sq. Ft.) | Roof Type | Date Installed | Deck Information | Age (Years) | Drainage 0-Good Slope/No Ponding 3-Low Slope/Some Ponding 5-Poor Slope/Ponding | Blisters 0-No Blisters 3-Less Than 20 Percent 5-More Than 20 Percent | Linear Folds/Cracks 0-No Folds/Cracks 3-Less Than 20 Percent 5-More Than 20 Percent | Flashing Condition 0-Good 3-Some Splits/Cracks 5-Poor Splits/Cracks Common | Leakage Problems 0-No leaks 3-Minor Leaks 5-Major Leaks | Surface Wear 0-No Wear Noted 3-Average Wear Noted 5-Excessive Wear Noted | Deck 0-Concrete 3-Metal 5-Wood | Total Score Condition | Estimated Service Life | Estimated Remaining Life
023 | Thoreau | R01 | R01 | 00R | ROOF | ROOF | 4752 | SIPLAST PARADIENE 20/30 FR | 1985-08-01 | 2.2" ISOCYANURATE, (2) LA | 41 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | -21
023 | Thoreau | R02 | R02 | 00R | ROOF | ROOF | 2622 | SIPLAST PARADIENE 20/30 FR | 1985-08-01 | 2.2" ISOCYANURATE, (2) LA | 41 | 0 | 3 | 0 | 3 | 0 | 5 | 0 | 11 | 20 | -21
023 | Thoreau | R03 | R03 | 00R | ROOF | ROOF | 588 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4
023 | Thoreau | R04 | R04 | 00R | ROOF | ROOF | 8948 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4
023 | Thoreau | R05 | R05 | 00R | ROOF | ROOF | 5454 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4
023 | Thoreau | R06 | R06 | 00R | ROOF | ROOF | 916 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4
023 | Thoreau | R07 | R07 | 00R | ROOF | ROOF | 5516 | SIPLAST PARADIENE 20/30 FR | 1985-08-01 | 2.2" ISOCYANURATE, (2) LA | 41 | 0 | 3 | 3 | 0 | 0 | 3 | 0 | 12 | 20 | -21
023 | Thoreau | R08 | R08 | 00R | ROOF | ROOF | 5196 | FIRESTONE EPDM W/BALLAST | 1992-08-01 | METAL | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | -19
023 | Thoreau | R09 | R09 | 00R | ROOF | ROOF | 1766 | FIRESTONE EPDM W/BALLAST | 1992-08-01 | METAL | 34 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 15 | -19
023 | Thoreau | R10 | R10 | 00R | ROOF | ROOF | 2204 | SIPLAST PARADIENE 20/30 FR | 1992-08-01 | METAL | 34 | 0 | 3 | 0 | 3 | 0 | 5 | 0 | 11 | 20 | -14
37962

## X026_R
Location Number | Location | Roof Identification Number | School Number | Level | Area Name | Roof Type | Area (Sq. Ft.) | Roof Type | Date Installed | Deck Information | Age (Years) | Drainage 0-Good Slope/No Ponding 3-Low Slope/Some Ponding 5-Poor Slope/Ponding | Blisters 0-No Blisters 3-Less Than 20 Percent 5-More Than 20 Percent | Linear Folds/Cracks 0-No Folds/Cracks 3-Less Than 20 Percent 5-More Than 20 Percent | Flashing Condition 0-Good 3-Some Splits/Cracks 5-Poor Splits/Cracks Common | Leakage Problems 0-No leaks 3-Minor Leaks 5-Major Leaks | Surface Wear 0-No Wear Noted 3-Average Wear Noted 5-Excessive Wear Noted | Deck 0-Concrete 3-Metal 5-Wood | Total Score Condition | Estimated Service Life | Estimated Remaining Life
026 | Randall | R01 | R01 | 00R | ROOF | ROOF | 2561 | MANVILLE 4GIG | 1998-08-01 | WOOD | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -8
026 | Randall | R02 | R02 | 00R | ROOF | ROOF | 4757 | MANVILLE 4GIG | 1998-08-01 | WOOD | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -8
026 | Randall | R03 | R03 | 00R | ROOF | ROOF | 1342 | CONCRETE TILE | 1998-08-01 | WOOD | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 22
026 | Randall | R04 | R04 | 00R | ROOF | ROOF | 4991 | CONCRETE TILE | 1998-08-01 | WOOD | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 22
026 | Randall | R05 | R05 | 00R | ROOF | ROOF | 3304 | CONCRETE TILE | 1998-08-01 | WOOD | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 22
026 | Randall | R06 | R06 | 00R | ROOF | ROOF | 4992 | CONCRETE TILE | 1998-08-01 | WOOD | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 22
026 | Randall | R07 | R07 | 00R | ROOF | ROOF | 1342 | CONCRETE TILE | 1998-08-01 | WOOD | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 22
23289

## X029_R
Location Number | Location | Roof Identification Number | School Number | Level | Area Name | Roof Type | Area (Sq. Ft.) | Roof Type | Date Installed | Deck Information | Age (Years) | Drainage 0-Good Slope/No Ponding 3-Low Slope/Some Ponding 5-Poor Slope/Ponding | Blisters 0-No Blisters 3-Less Than 20 Percent 5-More Than 20 Percent | Linear Folds/Cracks 0-No Folds/Cracks 3-Less Than 20 Percent 5-More Than 20 Percent | Flashing Condition 0-Good 3-Some Splits/Cracks 5-Poor Splits/Cracks Common | Leakage Problems 0-No leaks 3-Minor Leaks 5-Major Leaks | Surface Wear 0-No Wear Noted 3-Average Wear Noted 5-Excessive Wear Noted | Deck 0-Concrete 3-Metal 5-Wood | Total Score Condition | Estimated Service Life | Estimated Remaining Life
029 | Shorewood | C01 | C01 | 00R | CANOPY | CANOPY | 223 | GAF GAFGLAS 104G | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4
029 | Shorewood | C02 | C02 | 00R | CANOPY | CANOPY | 27 | GAF GAFGLAS 104G | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4
029 | Shorewood | C03 | C03 | 00R | CANOPY | CANOPY | 122 | GAF GAFGLAS 104G | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4
029 | Shorewood | C04 | C04 | 00R | CANOPY | CANOPY | 122 | SIPLAST PARADIENE 20/30 FR | 2003-08-01 | METAL | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -3
029 | Shorewood | C05 | C05 | 00R | CANOPY | CANOPY | 30 | SIPLAST PARADIENE 20/30 FR | 2003-08-01 | METAL | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -3
029 | Shorewood | R01 | R01 | 00R | ROOF | ROOF | 9354 | GAF GAFGLAS 104G | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4
029 | Shorewood | R02 | R02 | 00R | ROOF | ROOF | 3672 | 3-PLY TEMP | 1996-08-01 | METAL | 30 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 7 | -23
029 | Shorewood | R03 | R03 | 00R | ROOF | ROOF | 3017 | 3-PLY TEMP | 1996-08-01 | METAL | 30 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 7 | -23
029 | Shorewood | R04 | R04 | 00R | ROOF | ROOF | 1842 | SIPLAST PARADIENE 20/30 FR | 2003-08-01 | METAL | 23 | 3 | 3 | 0 | 0 | 0 | 3 | 0 | 12 | 20 | -3
029 | Shorewood | R05 | R05 | 00R | ROOF | ROOF | 8383 | SIPLAST PARADIENE 20/30 FR | 2003-08-01 | METAL | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -3
029 | Shorewood | R06 | R06 | 00R | ROOF | ROOF | 5358 | SIPLAST PARADIENE 20/30 FR | 2003-08-01 | METAL | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -3
029 | Shorewood | R07 | R07 | 00R | ROOF | ROOF | 3664 | GRACE GRM-500 | 1984-08-01 | TAMKO 15# FELT, 2.2" ISOC | 42 | 3 | 3 | 0 | 3 | 3 | 3 | 5 | 40 | 20 | -22
029 | Shorewood | R08 | R08 | 00R | ROOF | ROOF | 8664 | MODIFIED BIT. | 1990-08-01 | METAL | 36 | 3 | 3 | 3 | 0 | 3 | 3 | 3 | 39 | 20 | -16
44478

## X032_r
Location Number | Location | Roof Identification Number | School Number | Level | Area Name | Roof Type | Area (Sq. Ft.) | Roof Type | Date Installed | Deck Information | Age (Years) | Drainage 0-Good Slope/No Ponding 3-Low Slope/Some Ponding 5-Poor Slope/Ponding | Blisters 0-No Blisters 3-Less Than 20 Percent 5-More Than 20 Percent | Linear Folds/Cracks 0-No Folds/Cracks 3-Less Than 20 Percent 5-More Than 20 Percent | Flashing Condition 0-Good 3-Some Splits/Cracks 5-Poor Splits/Cracks Common | Leakage Problems 0-No leaks 3-Minor Leaks 5-Major Leaks | Surface Wear 0-No Wear Noted 3-Average Wear Noted 5-Excessive Wear Noted | Deck 0-Concrete 3-Metal 5-Wood | Total Score Condition | Estimated Service Life | Estimated Remaining Life
032 | Stephens | R01 | R01 | 00R | ROOF | ROOF | 19806 | MANVILLE-DYNAKAP | 1986-08-01 | METAL | 40 | 0 | 0 | 0 | 3 | 3 | 3 | 3 | 27 | 20 | -20
032 | Stephens | R02 | R02 | 00R | ROOF | ROOF | 16559 | MANVILLE-DYNAKAP | 1986-08-01 | METAL | 40 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 6 | 20 | -20
032 | Stephens | R03 | R03 | 00R | GYM ROOF | ROOF | 4382 | MANVILLE-DYNAKAP | 1986-08-01 | METAL | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -20
032 | Stephens | R04 | R04 | 00R | LMC ROOF AREA | ROOF | 8723 | MANVILLE-DYNAKAP-3CIG | 1990-08-01 | UNKNOWN | 36 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 6 | 20 | -16
032 | Stephens | R05 | R05 | 00R | ROOF | ROOF | 517 | GAF GAFGLAS 104G | 1993-08-01 | UNKNOWN | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -13
032 | Stephens | R06 | R06 | 00R | ROOF | ROOF | 2754 | GAF GAFGLAS 104G | 1993-08-01 | UNKNOWN | 33 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 6 | 20 | -13
032 | Stephens | R07 | R07 | 00R | GYM ROOF | ROOF | 8779 | GAF GAFGLAS 104G | 1993-08-01 | UNKNOWN | 33 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -13
032 | Stephens | R08 | R08 | 00R | ROOF | ROOF | 16237 | GAF GAFGLAS 104G | 1993-08-01 | UNKNOWN | 33 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 6 | 20 | -13
032 | Stephens | R09 | R09 | 00R | ROOF | ROOF | 1808 | GAF GAFGLAS 104G | 1993-08-01 | UNKNOWN | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -13
79565

## X036_R
Location Number | Location | Roof Identification Number | School Number | Level | Area Name | Roof Type | Area (Sq. Ft.) | Roof Type | Date Installed | Deck Information | Age (Years) | Drainage 0-Good Slope/No Ponding 3-Low Slope/Some Ponding 5-Poor Slope/Ponding | Blisters 0-No Blisters 3-Less Than 20 Percent 5-More Than 20 Percent | Linear Folds/Cracks 0-No Folds/Cracks 3-Less Than 20 Percent 5-More Than 20 Percent | Flashing Condition 0-Good 3-Some Splits/Cracks 5-Poor Splits/Cracks Common | Leakage Problems 0-No leaks 3-Minor Leaks 5-Major Leaks | Surface Wear 0-No Wear Noted 3-Average Wear Noted 5-Excessive Wear Noted | Deck 0-Concrete 3-Metal 5-Wood | Total Score Condition | Estimated Service Life | Estimated Remaining Life
036 | Kennedy | R01 | R01 | 00R | ROOF | ROOF | 6131 | SIPLAST PARADIENE 20/30 FR | 1987-08-01 | CONCRETE | 39 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | -19
036 | Kennedy | R02 | R02 | 00R | ROOF | ROOF | 4877 | SIPLAST PARADIENE 20/30 FR | 2004-08-04 | CONCRETE | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -2
036 | Kennedy | R03 | R03 | 00R | ROOF | ROOF | 4530 | MANVILLE GLASPLY-IV 4-PLY | 1991-08-01 | METAL | 35 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -15
036 | Kennedy | R04 | R04 | 00R | ROOF | ROOF | 4701 | MANVILLE GLASPLY-IV 4-PLY | 1991-08-01 | METAL | 35 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -15
036 | Kennedy | R05 | R05 | 00R | ROOF | ROOF | 6117 | SIPLAST PARADIENE 20/30 FR | 2004-08-04 | CONCRETE | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -2
036 | Kennedy | R06 | R06 | 00R | ROOF | ROOF | 1323 | MANVILLE GLASPLY-IV 4-PLY | 1991-08-01 | METAL | 35 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 6 | 20 | -15
036 | Kennedy | R07 | R07 | 00R | ROOF | ROOF | 7823 | MANVILLE GLASPLY-IV 4-PLY | 1991-08-01 | METAL | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -15
35502

## X037_r
Location Number | Location | Roof Identification Number | School Number | Level | Area Name | Roof Type | Area (Sq. Ft.) | Roof Type | Date Installed | Deck Information | Age (Years) | Drainage 0-Good Slope/No Ponding 3-Low Slope/Some Ponding 5-Poor Slope/Ponding | Blisters 0-No Blisters 3-Less Than 20 Percent 5-More Than 20 Percent | Linear Folds/Cracks 0-No Folds/Cracks 3-Less Than 20 Percent 5-More Than 20 Percent | Flashing Condition 0-Good 3-Some Splits/Cracks 5-Poor Splits/Cracks Common | Leakage Problems 0-No leaks 3-Minor Leaks 5-Major Leaks | Surface Wear 0-No Wear Noted 3-Average Wear Noted 5-Excessive Wear Noted | Deck 0-Concrete 3-Metal 5-Wood | Total Score Condition | Estimated Service Life | Estimated Remaining Life
037 | Lincoln | R01 | R01 | 00R | ROOF | ROOF | 7818 | CELOTEX-CELOPAL-I | 1986-08-01 | METAL | 40 | 0 | 5 | 0 | 0 | 0 | 3 | 0 | 8 | 20 | -20
037 | Lincoln | R02 | R02 | 00R | ROOF | ROOF | 6245 | CELOTEX-CELOPAL-I | 1986-08-01 | METAL | 40 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -20
037 | Lincoln | R03 | R03 | 00R | ROOF | ROOF | 6397 | CELOTEX-CELOPAL-I | 1986-08-01 | METAL | 40 | 1 | 3 | 0 | 0 | 0 | 3 | 0 | 8 | 20 | -20
037 | Lincoln | R04 | R04 | 00R | ROOF | ROOF | 3004 | CELOTEX-CELOPAL-I | 1986-08-01 | METAL | 40 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -20
037 | Lincoln | R05 | R05 | 00R | ADDITION - ROOF | ROOF | 5916 | BUR W/ PEA GRAVEL | 2000-08-01 | METAL | 26 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -6
037 | Lincoln | R06 | R06 | 00R | ROOF | ROOF | 5272 | CELOTEX-CELOPAL-I | 1986-08-01 | METAL | 40 | 0 | 3 | 1 | 3 | 0 | 3 | 0 | 11 | 20 | -20
037 | Lincoln | R07 | R07 | 00R | ROOF | ROOF | 4941 | CELOTEX-CELOPAL-I | 1986-08-01 | METAL | 40 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | -20
037 | Lincoln | R08 | R08 | 00R | ROOF | ROOF | 6951 | CELOTEX-CELOPAL-I | 1986-08-01 | METAL | 40 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -20
037 | Lincoln | R09 | R09 | 00R | ROOF | ROOF | 5728 | CELOTEX-CELOPAL-I | 1986-08-01 | METAL | 40 | 0 | 3 | 2 | 2 | 0 | 3 | 0 | 12 | 20 | -20
037 | Lincoln | R10 | R10 | 00R | ROOF | ROOF | 4047 | CELOTEX-CELOPAL-I | 1986-08-01 | METAL | 40 | 0 | 2 | 0 | 0 | 0 | 4 | 0 | 6 | 20 | -20
037 | Lincoln | R11 | R11 | 00R | ROOF | ROOF | 11011 | CELOTEX-CELOPAL-I | 1986-08-01 | METAL | 40 | 0 | 1 | 0 | 0 | 0 | 4 | 0 | 5 | 20 | -20

## X038_r
Location Number | Location | Roof Identification Number | School Number | Level | Area Name | Roof Type | Area (Sq. Ft.) | Roof Type | Date Installed | Deck Information | Age (Years) | Drainage 0-Good Slope/No Ponding 3-Low Slope/Some Ponding 5-Poor Slope/Ponding | Blisters 0-No Blisters 3-Less Than 20 Percent 5-More Than 20 Percent | Linear Folds/Cracks 0-No Folds/Cracks 3-Less Than 20 Percent 5-More Than 20 Percent | Flashing Condition 0-Good 3-Some Splits/Cracks 5-Poor Splits/Cracks Common | Leakage Problems 0-No leaks 3-Minor Leaks 5-Major Leaks | Surface Wear 0-No Wear Noted 3-Average Wear Noted 5-Excessive Wear Noted | Deck 0-Concrete 3-Metal 5-Wood | Total Score Condition | Estimated Service Life | Estimated Remaining Life
038 | Huegel | R01 | R01 | 00R | ROOF | ROOF | 4800 | CELOTEX-4-PLY-BUIT-UP | 1991-08-01 | METAL | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -15
038 | Huegel | R02 | R02 | 00R | ROOF | ROOF | 832 | CELOTEX-4-PLY-BUIT-UP | 1991-08-01 | METAL | 35 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2 | 20 | -15
038 | Huegel | R03 | R03 | 00R | ROOF | ROOF | 16349 | CELOTEX-4-PLY-BUIT-UP | 1991-08-01 | METAL | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -15
038 | Huegel | R04 | R04 | 00R | ROOF | ROOF | 310 | CELOTEX-4-PLY-BUIT-UP | 1991-08-01 | METAL | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -15
038 | Huegel | R05 | R05 | 00R | ROOF | ROOF | 5750 | CELOTEX-4-PLY-BUIT-UP | 1991-08-01 | METAL | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -15
038 | Huegel | R06 | R06 | 00R | ROOF | ROOF | 461 | CELOTEX-4-PLY-BUIT-UP | 1991-08-01 | METAL | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -15
038 | Huegel | R07 | R07 | 00R | ROOF | ROOF | 695 | CELOTEX-4-PLY-BUIT-UP | 1991-08-01 | METAL | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -15
038 | Huegel | R08 | R08 | 00R | ROOF | ROOF | 229 | CELOTEX-4-PLY-BUIT-UP | 1991-08-01 | METAL | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -15
038 | Huegel | R09 | R09 | 00R | ROOF | ROOF | 2135 | CELOTEX-4-PLY-BUIT-UP | 1991-08-01 | METAL | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -15
038 | Huegel | R10 | R10 | 00R | ROOF | ROOF | 443 | MANVILLE GLASPLY-IV 4-PLY | 1993-08-01 | WOOD | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -13
038 | Huegel | R11 | R11 | 00R | ROOF | ROOF | 2169 | MANVILLE GLASPLY-IV 4-PLY | 1993-08-01 | WOOD | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -13
038 | Huegel | R12 | R12 | 00R | ROOF | ROOF | 1795 | MANVILLE GLASPLY-IV 4-PLY | 1993-08-01 | WOOD | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -13
038 | Huegel | R13 | R13 | 00R | ROOF | ROOF | 419 | MANVILLE GLASPLY-IV 4-PLY | 1993-08-01 | WOOD | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -13
038 | Huegel | R14 | R14 | 00R | ROOF | ROOF | 2217 | MANVILLE GLASPLY-IV 4-PLY | 1993-08-01 | WOOD | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -13
038 | Huegel | R15 | R15 | 00R | ROOF | ROOF | 1469 | MANVILLE GLASPLY-IV 4-PLY | 1993-08-01 | WOOD | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -13
038 | Huegel | R16 | R16 | 00R | ROOF | ROOF | 906 | MANVILLE GLASPLY-IV 4-PLY | 1993-08-01 | WOOD | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -13
038 | Huegel | R17 | R17 | 00R | ROOF | ROOF | 1472 | MANVILLE GLASPLY-IV 4-PLY | 1993-08-01 | WOOD | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -13
038 | Huegel | R18 | R18 | 00R | ROOF | ROOF | 2179 | MANVILLE GLASPLY-IV 4-PLY | 1993-08-01 | WOOD | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -13
038 | Huegel | R19 | R19 | 00R | ROOF | ROOF | 9084 | MANVILLE GLASPLY-IV 4-PLY | 1993-08-01 | WOOD | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -13
038 | Huegel | R20 | R20 | 00R | ROOF | ROOF | 1829 | MANVILLE GLASPLY-IV 4-PLY | 1993-08-01 | WOOD | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -13
038 | Huegel | R21 | R21 | 00R | ROOF | ROOF | 819 | MANVILLE GLASPLY-IV 4-PLY | 1993-08-01 | WOOD | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -13
038 | Huegel | R22 | R22 | 00R | ROOF | ROOF | 326 | CELOTEX-4-PLY-BUIT-UP | 1991-08-01 | METAL | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -15
038 | Huegel | R23 | R23 | 00R | ROOF | ROOF | 651 | MANVILLE GLASPLY-IV 4-PLY | 1993-08-01 | WOOD | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -13
038 | Huegel | R24 | R24 | 00R | ROOF | ROOF | 3377 | MANVILLE GLASPLY-IV 4-PLY | 1993-08-01 | WOOD | 33 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 6 | 20 | -13
038 | Huegel | R25 | R25 | 00R | ROOF | ROOF | 650 | MANVILLE GLASPLY-IV 4-PLY | 1993-08-01 | WOOD | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -13
61366

## X052_r
Location Number | Location | Roof Identification Number | School Number | Level | Area Name | Roof Type | Area (Sq. Ft.) | Roof Type | Date Installed | Deck Information | Age (Years) | Drainage 0-Good Slope/No Ponding 3-Low Slope/Some Ponding 5-Poor Slope/Ponding | Blisters 0-No Blisters 3-Less Than 20 Percent 5-More Than 20 Percent | Linear Folds/Cracks 0-No Folds/Cracks 3-Less Than 20 Percent 5-More Than 20 Percent | Flashing Condition 0-Good 3-Some Splits/Cracks 5-Poor Splits/Cracks Common | Leakage Problems 0-No leaks 3-Minor Leaks 5-Major Leaks | Surface Wear 0-No Wear Noted 3-Average Wear Noted 5-Excessive Wear Noted | Deck 0-Concrete 3-Metal 5-Wood | Total Score Condition | Estimated Service Life | Estimated Remaining Life
052 | Chavez | R01 | R01 | 00R | GYM | ROOF | 9895 | SIPLAST PARADIENE 20/30 FR | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5
052 | Chavez | R02 | R02 | 00R | CANOPY | ROOF | 52 | SIPLAST PARADIENE 20/30 FR | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5
052 | Chavez | R03 | R03 | 00R | ADMINISTRATIVE | ROOF | 5915 | SIPLAST PARADIENE 20/30 FR | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5
052 | Chavez | R04 | R04 | 00R | ROOF | ROOF | 1056 | SIPLAST PARADIENE 20/30 FR | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5
052 | Chavez | R05 | R05 | 00R | THIRD-GRADE | ROOF | 6543 | SIPLAST PARADIENE 20/30 FR | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5
052 | Chavez | R06 | R06 | 00R | CAFE-LMC | ROOF | 7709 | SIPLAST PARADIENE 20/30 FR | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5
052 | Chavez | R07 | R07 | 00R | MECHANICAL | ROOF | 1778 | SIPLAST PARADIENE 20/30 FR | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5
052 | Chavez | R08 | R08 | 00R | ROOF | ROOF | 2908 | SIPLAST PARADIENE 20/30 FR | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5
052 | Chavez | R09 | R09 | 00R | CANOPY | ROOF | 226 | SIPLAST PARADIENE 20/30 FR | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5
052 | Chavez | R10 | R10 | 00R | FOURTH-GRADE | ROOF | 9366 | SIPLAST PARADIENE 20/30 FR | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5
052 | Chavez | R11 | R11 | 00R | KINDERGARTEN | ROOF | 609 | SIPLAST PARADIENE 20/30 FR | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5
052 | Chavez | R12 | R12 | 00R | CANOPY | ROOF | 226 | SIPLAST PARADIENE 20/30 FR | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5
052 | Chavez | R13 | R13 | 00R | FIFTH-GRADE | ROOF | 6367 | SIPLAST PARADIENE 20/30 FR | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5
052 | Chavez | R14 | R14 | 00R | ROOF | ROOF | 1043 | SIPLAST PARADIENE 20/30 FR | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5
052 | Chavez | R15 | R15 | 00R | RECEIVING | ROOF | 3384 | SIPLAST PARADIENE 20/30 FR | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5
57077

## X053_R
Location Number | Location | Roof Identification Number | School Number | Level | Area Name | Roof Type | Area (Sq. Ft.) | Roof Type | Date Installed | Deck Information | Age (Years) | Drainage 0-Good Slope/No Ponding 3-Low Slope/Some Ponding 5-Poor Slope/Ponding | Blisters 0-No Blisters 3-Less Than 20 Percent 5-More Than 20 Percent | Linear Folds/Cracks 0-No Folds/Cracks 3-Less Than 20 Percent 5-More Than 20 Percent | Flashing Condition 0-Good 3-Some Splits/Cracks 5-Poor Splits/Cracks Common | Leakage Problems 0-No leaks 3-Minor Leaks 5-Major Leaks | Surface Wear 0-No Wear Noted 3-Average Wear Noted 5-Excessive Wear Noted | Deck 0-Concrete 3-Metal 5-Wood | Total Score Condition | Estimated Service Life | Estimated Remaining Life
053 | Sandburg | R01 | R01 | 00R | ROOF | ROOF | 38590 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | 1/2" WOOD FIBER, (2) LAYE | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4
053 | Sandburg | R02 | R02 | 00R | GYM ROOF | ROOF | 4586 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | 1/2" WOOD FIBER, (2) LAYE | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4
053 | Sandburg | R03 | R03 | 00R | ADDITION | ROOF | 5011 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | 1/2" WOOD FIBER, (2) LAYE | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4
053 | Sandburg | R04 | R04 | 00R | RELOCATABLE ROOF | ROOF | 860 | BUR 4-PLY | 2003-08-01 | PLYWOOD DECK | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -3
49047

## X071_r
Location Number | Location | Roof Identification Number | School Number | Level | Area Name | Roof Type | Area (Sq. Ft.) | Roof Type | Date Installed | Deck Information | Age (Years) | Drainage 0-Good Slope/No Ponding 3-Low Slope/Some Ponding 5-Poor Slope/Ponding | Blisters 0-No Blisters 3-Less Than 20 Percent 5-More Than 20 Percent | Linear Folds/Cracks 0-No Folds/Cracks 3-Less Than 20 Percent 5-More Than 20 Percent | Flashing Condition 0-Good 3-Some Splits/Cracks 5-Poor Splits/Cracks Common | Leakage Problems 0-No leaks 3-Minor Leaks 5-Major Leaks | Surface Wear 0-No Wear Noted 3-Average Wear Noted 5-Excessive Wear Noted | Deck 0-Concrete 3-Metal 5-Wood | Total Score Condition | Estimated Service Life | Estimated Remaining Life
071 | Lindbergh | R01 | R01 | 00R | ROOF | ROOF | 10297 | SIPLAST PARADIENE 20/30 FR | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5
071 | Lindbergh | R02 | R02 | 00R | ROOF | ROOF | 15558 | SIPLAST PARADIENE 20/30 FR | 1987-08-01 | METAL | 39 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 42 | 20 | -19
071 | Lindbergh | R03 | R03 | 00R | ROOF | ROOF | 3486 | SIPLAST PARADIENE 20/30 FR | 1986-08-01 | METAL | 40 | 3 | 3 | 3 | 3 | 0 | 3 | 0 | 21 | 20 | -20
071 | Lindbergh | R04 | R04 | 00R | ROOF | ROOF | 4474 | SIPLAST PARADIENE 20/30 FR | 1984-08-01 | METAL | 42 | 3 | 3 | 0 | 3 | 0 | 3 | 0 | 15 | 20 | -22
33815

## R072_R
Location Number | Location | Roof Identification Number | School Number | Level | Area Name | Roof Type | Area (Sq. Ft.) | Roof Type | Date Installed | Deck Information | Age (Years) | Drainage 0-Good Slope/No Ponding 3-Low Slope/Some Ponding 5-Poor Slope/Ponding | Blisters 0-No Blisters 3-Less Than 20 Percent 5-More Than 20 Percent | Linear Folds/Cracks 0-No Folds/Cracks 3-Less Than 20 Percent 5-More Than 20 Percent | Flashing Condition 0-Good 3-Some Splits/Cracks 5-Poor Splits/Cracks Common | Leakage Problems 0-No leaks 3-Minor Leaks 5-Major Leaks | Surface Wear 0-No Wear Noted 3-Average Wear Noted 5-Excessive Wear Noted | Deck 0-Concrete 3-Metal 5-Wood | Total Score Condition | Estimated Service Life | Estimated Remaining Life
072 | Leopold | R01 | R01 | 00R | ROOF | ROOF | 3853 | SIPLAST PARADIENE 20/30 FR | 1986-08-01 | METAL | 40 | 0 | 5 | 3 | 0 | 0 | 3 | 0 | 14 | 20 | -20
072 | Leopold | R02 | R02 | 00R | ROOF | ROOF | 46 | SIPLAST PARADIENE 20/30 FR | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5
072 | Leopold | R03 | R03 | 00R | ROOF | ROOF | 12071 | SIPLAST PARADIENE 20/30 FR | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5
072 | Leopold | R04 | R04 | 00R | ROOF | ROOF | 39 | SIPLAST PARADIENE 20/30 FR | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5
072 | Leopold | R05 | R05 | 00R | ROOF | ROOF | 2454 | MANVILLE DYNAKAP FR | 1990-08-01 | METAL | 36 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -16
072 | Leopold | R06 | R06 | 00R | ROOF | ROOF | 4520 | MANVILLE DYNAKAP FR | 1990-08-01 | METAL | 36 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -16
072 | Leopold | R07 | R07 | 00R | ROOF | ROOF | 7275 | SIPLAST PARADIENE 20/30 FR | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5
072 | Leopold | R08 | R08 | 00R | ROOF | ROOF | 127 | SIPLAST PARADIENE 20/30 FR | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5
072 | Leopold | R09 | R09 | 00R | ROOF | ROOF | 16719 | SIPLAST PARADIENE 20/30 FR | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5
072 | Leopold | R10 | R10 | 00R | ROOF | ROOF | 4898 | EPDM BALLAST | 2003-03-01 | METAL | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | -8
072 | Leopold | R11 | R11 | 00R | ROOF | ROOF | 358 | EPDM BALLAST | 2003-03-01 | METAL | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | -8
072 | Leopold | R12 | R12 | 00R | ROOF | LMC ROOF | 2422 | EPDM BALLAST | 2003-03-01 | METAL | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | -8
072 | Leopold | R13 | R13 | 00R | ROOF | ROOF | 462 | EPDM BALLAST | 2003-03-01 | METAL | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | -8
072 | Leopold | R14 | R14 | 00R | ROOF | ROOF | 7207 | EPDM BALLAST | 2003-03-01 | METAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 15
62451

## R007_R
Location Number | Location | Roof Identification Number | School Number | Level | Area Name | Roof Type | Area (Sq. Ft.) | Roof Type | Date Installed | Deck Information | Age (Years) | Drainage 0-Good Slope/No Ponding 3-Low Slope/Some Ponding 5-Poor Slope/Ponding | Blisters 0-No Blisters 3-Less Than 20 Percent 5-More Than 20 Percent | Linear Folds/Cracks 0-No Folds/Cracks 3-Less Than 20 Percent 5-More Than 20 Percent | Flashing Condition 0-Good 3-Some Splits/Cracks 5-Poor Splits/Cracks Common | Leakage Problems 0-No leaks 3-Minor Leaks 5-Major Leaks | Surface Wear 0-No Wear Noted 3-Average Wear Noted 5-Excessive Wear Noted | Deck 0-Concrete 3-Metal 5-Wood | Total Score Condition | Estimated Service Life | Estimated Remaining Life
007 | Emerson | R01 | R01 | 00R | ROOF | ROOF | 8474 | SIPLAST PARADIENE 30 FR | 1990-08-01 | WOOD | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -16
007 | Emerson | R02 | R02 | 00R | ROOF | ROOF | 9012 | SIPLAST PARADIENE 20 | 1992-08-01 | 2.3" ISO, 1" PERLITE, CON | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14
007 | Emerson | R03 | R03 | 00R | ROOF | ROOF | 1326 | SIPLAST PARADIENE 30 FR | 1990-08-01 | WOOD | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -16
007 | Emerson | R04 | R04 | 00R | ROOF | ROOF | 647 | SIPLAST PARADIENE 30 FR | 1990-08-01 | 1.5" ISO, 1.5" COMP INS, | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -16
007 | Emerson | R05 | R05 | 00R | ROOF | ROOF | 1334 | SIPLAST PARADIENE 20 | 1992-08-01 | 2.3" ISO, 1" PERLITE, CON | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14
007 | Emerson | R06 | R06 | 00R | ROOF | ROOF | 1148 | SIPLAST PARADIENE 30 FR | 1990-08-01 | WOOD | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -16
007 | Emerson | R07 | R07 | 00R | ROOF | ROOF | 3511 | MANVILLE 4-PLY BUR | 1992-08-01 | WOOD | 34 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 3 | 20 | -14
25452

## X203_r
Location Number | Location | Roof Identification Number | School Number | Level | Area Name | Roof Type | Area (Sq. Ft.) | Roof Type | Date Installed | Deck Information | Age (Years) | Drainage 0-Good Slope/No Ponding 3-Low Slope/Some Ponding 5-Poor Slope/Ponding | Blisters 0-No Blisters 3-Less Than 20 Percent 5-More Than 20 Percent | Linear Folds/Cracks 0-No Folds/Cracks 3-Less Than 20 Percent 5-More Than 20 Percent | Flashing Condition 0-Good 3-Some Splits/Cracks 5-Poor Splits/Cracks Common | Leakage Problems 0-No leaks 3-Minor Leaks 5-Major Leaks | Surface Wear 0-No Wear Noted 3-Average Wear Noted 5-Excessive Wear Noted | Deck 0-Concrete 3-Metal 5-Wood | Total Score Condition | Estimated Service Life | Estimated Remaining Life
203 | Cherokee | R01 | R01 | 00R | ROOF | ROOF | 15998 | EPDM BALLAST | 1984-08-01 | METAL | 42 | 3 | 0 | 0 | 0 | 3 | 3 | 3 | 30 | 15 | -27
203 | Cherokee | R02 | R02 | 00R | ROOF | ROOF | 11017 | EPDM BALLAST | 1984-08-01 | METAL | 42 | 3 | 0 | 0 | 0 | 3 | 3 | 3 | 30 | 15 | -27
203 | Cherokee | R03 | R03 | 00R | ROOF | ROOF | 18103 | SIPLAST PARADIENE 20/30 FR TG | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5
203 | Cherokee | R04 | R04 | 00R | ROOF | ROOF | 281 | SIPLAST PARADIENE 20/30 FR TG | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5
203 | Cherokee | R05 | R05 | 00R | ROOF | ROOF | 910 | SIPLAST PARADIENE 20/30 FR TG | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5
203 | Cherokee | R06 | R06 | 00R | ROOF | ROOF | 4056 | SIPLAST PARADIENE 20/30 FR TG | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5
203 | Cherokee | R07 | R07 | 00R | ROOF | ROOF | 327 | SIPLAST PARADIENE 20/30 FR TG | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5
50692

## X210_r
Location Number | Location | Roof Identification Number | School Number | Level | Area Name | Roof Type | Area (Sq. Ft.) | Roof Type | Date Installed | Deck Information | Age (Years) | Drainage 0-Good Slope/No Ponding 3-Low Slope/Some Ponding 5-Poor Slope/Ponding | Blisters 0-No Blisters 3-Less Than 20 Percent 5-More Than 20 Percent | Linear Folds/Cracks 0-No Folds/Cracks 3-Less Than 20 Percent 5-More Than 20 Percent | Flashing Condition 0-Good 3-Some Splits/Cracks 5-Poor Splits/Cracks Common | Leakage Problems 0-No leaks 3-Minor Leaks 5-Major Leaks | Surface Wear 0-No Wear Noted 3-Average Wear Noted 5-Excessive Wear Noted | Deck 0-Concrete 3-Metal 5-Wood | Total Score Condition | Estimated Service Life | Estimated Remaining Life
210 | Blackhawk | PH01 | PH01 | 00R | PENTHOUSE | ROOF | 1269 | BUR 4-PLY | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4
210 | Blackhawk | PH02 | PH02 | 00R | PENTHOUSE | ROOF | 2256 | BUR 4-PLY | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4
210 | Blackhawk | R01 | R01 | 00R | ROOF | ROOF | 3313 | BUR 4-PLY | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4
210 | Blackhawk | R02 | R02 | 00R | ROOF | ROOF | 5198 | BUR 4-PLY | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4
210 | Blackhawk | R03 | R03 | 00R | ROOF | ROOF | 2298 | BUR 4-PLY | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4
210 | Blackhawk | R04 | R04 | 00R | ROOF | ROOF | 7673 | BUR 4-PLY | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4
210 | Blackhawk | R05 | R05 | 00R | ROOF | ROOF | 10807 | BUR 4-PLY | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4
210 | Blackhawk | R07 | R07 | 00R | ROOF | ROOF | 7227 | BUR 4-PLY | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4
210 | Blackhawk | R08 | R08 | 00R | ROOF | ROOF | 8498 | BUR 4-PLY | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4
210 | Blackhawk | R09 | R09 | 00R | ROOF | ROOF | 5734 | SIPLAST PARADIENE 20/30 FR | 1990-08-01 | METAL | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -16
210 | Blackhawk | R10 | R10 | 00R | ROOF | ROOF | 11284 | BUR 4-PLY | 2002-08-01 | UNKNOWN | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4
210 | Blackhawk | R11 | R11 | 00R | ROOF | ROOF | 8371 | BUR 4-PLY | 2002-08-01 | UNKNOWN | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4
210 | Blackhawk | R12 | R12 | 00R | ROOF | ROOF | 1740 | DERBIGUM HPS, COMP INS (2 | 1983-08-01 | METAL | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -23
210 | Blackhawk | R13 | R13 | 00R | ROOF | ROOF | 2960 | SIPLAST PARADIENE 20/30 FR | 2003-08-01 | CONCRETE | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -3
210 | Blackhawk | R14 | R14 | 00R | ROOF | ROOF | 419 | SIPLAST PARADIENE 20/30 FR | 2003-08-01 | METAL | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -3
210 | Blackhawk | R15 | R15 | 00R | ROOF | ROOF | 8538 | GAF GAFGLAS 4-PLY W/GRAV | 1991-08-01 | WOOD | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -15
210 | Blackhawk | R16 | R16 | 00R | ROOF | ROOF | 30712 | GAF GAFGLAS 4-PLY W/GRAV | 1991-08-01 | WOOD | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -15
210 | Blackhawk | R17 | R17 | 00R | RELOCATABLE NORTH | ROOF | 1053 | UNKNOWN | 1965-08-01 | UNKNOWN | 61 | 0 | 0 | 0 | 5 | 3 | 3 | 5 | 33 | 15 | -46
210 | Blackhawk | R18 | R18 | 00R | RELOCATABLE EAST | ROOF | 1227 | UNKNOWN | 1965-08-01 | UNKNOWN | 61 | 0 | 0 | 0 | 5 | 3 | 3 | 5 | 33 | 15 | -46
120577

## R220_r
Location Number | Location | Roof Identification Number | School Number | Level | Area Name | Roof Type | Area (Sq. Ft.) | Roof Type | Date Installed | Deck Information | Age (Years) | Drainage 0-Good Slope/No Ponding 3-Low Slope/Some Ponding 5-Poor Slope/Ponding | Blisters 0-No Blisters 3-Less Than 20 Percent 5-More Than 20 Percent | Linear Folds/Cracks 0-No Folds/Cracks 3-Less Than 20 Percent 5-More Than 20 Percent | Flashing Condition 0-Good 3-Some Splits/Cracks 5-Poor Splits/Cracks Common | Leakage Problems 0-No leaks 3-Minor Leaks 5-Major Leaks | Surface Wear 0-No Wear Noted 3-Average Wear Noted 5-Excessive Wear Noted | Deck 0-Concrete 3-Metal 5-Wood | Total Score Condition | Estimated Service Life | Estimated Remaining Life
220 | O'Keeffe | R01 | R01 | 00R | ROOF | ROOF | 7710 | SCHULLER 2FID MODIFIED | 1995-08-01 | UNKNOWN | 31 | 0 | 3 | 3 | 3 | 0 | 3 | 0 | 15 | 20 | -11
220 | O'Keeffe | R02 | R02 | 00R | ROOF | ROOF | 10105 | SCHULLER 2FID MODIFIED | 1996-08-01 | UNKNOWN | 30 | 3 | 3 | 0 | 0 | 0 | 0 | 0 | 9 | 20 | -10
220 | O'Keeffe | R03 | R03 | 00R | ROOF | ROOF | 1648 | SIPLAST PARADIENE 20/30 FR | 1985-08-01 | METAL | 41 | 0 | 3 | 3 | 0 | 0 | 3 | 0 | 12 | 20 | -21
220 | O'Keeffe | R04 | R04 | 00R | ROOF | ROOF | 3445 | EPDM BALLAST | 1986-08-01 | WOOD | 40 | 0 | 0 | 0 | 3 | 3 | 3 | 5 | 31 | 15 | -25
220 | O'Keeffe | R05 | R05 | 00R | ROOF | ROOF | 2849 | SIPLAST PARADIENE 20/30 FR | 1986-08-01 | METAL | 40 | 3 | 3 | 0 | 0 | 0 | 3 | 0 | 12 | 20 | -20
220 | O'Keeffe | R06 | R06 | 00R | ROOF | ROOF | 7091 | MANVILLE 4-PLY BUR | 1994-08-01 | METAL | 32 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -12
220 | O'Keeffe | R07 | R07 | 00R | ROOF | ROOF | 1139 | SIPLAST PARADIENE 20/30 FR | 1998-08-01 | UNKNOWN | 28 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -8
220 | O'Keeffe | R08 | R08 | 00R | ROOF | ROOF | 1323 | SIPLAST PARADIENE 20/30 FR | 1998-08-01 | PRECAST CONCRETE | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -8
220 | O'Keeffe | R09 | R09 | 00R | ROOF | ROOF | 1684 | SCHULLER 2FID MODIFIED | 1996-08-01 | UNKNOWN | 30 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -10
220 | O'Keeffe | R10 | R10 | 00R | ROOF | ROOF | 1752 | SIPLAST PARADIENE 20/30 FR | 1998-08-01 | PRECAST CONCRETE | 28 | 3 | 0 | 0 | 0 | 0 | 1 | 0 | 7 | 20 | -8
220 | O'Keeffe | R11 | R11 | 00R | ROOF | ROOF | 7090 | SIPLAST PARADIENE 20/30 FR | 1998-08-01 | METAL | 28 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -8
220 | O'Keeffe | R12 | R12 | 00R | ROOF | ROOF | 4871 | SIPLAST PARADIENE 20/30 FR | 1998-08-01 | METAL | 28 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -8
220 | O'Keeffe | R13 | R13 | 00R | ROOF | ROOF | 3257 | SIPLAST PARADIENE 20/30 FR | 1998-08-01 | PRECAST CONCRETE | 28 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -8
220 | O'Keeffe | R14 | R14 | 00R | ROOF | ROOF | 2128 | SIPLAST PARADIENE 20/30 FR | 1998-08-01 | UNKNOWN | 28 | 5 | 0 | 0 | 0 | 0 | 3 | 0 | 13 | 20 | -8
220 | O'Keeffe | R15 | R15 | 00R | MECH. ROOM | ROOF | 748 | SIPLAST PARADIENE 20/30 FR | 1998-08-01 | METAL | 28 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -8
220 | O'Keeffe | R16 | R16 | 00R | FIELD HOUSE NORTHWEST | ROOF | 2877 | SIPLAST PARADIENE 20/30 FR | 1990-08-01 | CEMENTITIOUS WOOD FIBER | 36 | 0 | 3 | 0 | 0 | 0 | 5 | 0 | 8 | 20 | -16
220 | O'Keeffe | R17 | R17 | 00R | FIELD HOUSE NORTH EAST | ROOF | 2959 | SIPLAST PARADIENE 20/30 FR | 1990-08-01 | CEMENTITIOUS WOOD FIBER | 36 | 0 | 3 | 0 | 0 | 0 | 5 | 0 | 8 | 20 | -16
220 | O'Keeffe | R18 | R18 | 00R | FIELD HOUSE SOUTH EAST | ROOF | 2892 | SIPLAST PARADIENE 20/30 FR | 1990-08-01 | CEMENTITIOUS WOOD FIBER | 36 | 0 | 3 | 0 | 0 | 0 | 5 | 0 | 8 | 20 | -16
220 | O'Keeffe | R19 | R19 | 00R | FIELD HOUSE SOUTH WEST | ROOF | 2798 | SIPLAST PARADIENE 20/30 FR | 1990-08-01 | CEMENTITIOUS WOOD FIBER | 36 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | 20 | -16
220 | O'Keeffe | R20 | R20 | 00R | ROOF | ROOF | 2146 | SIPLAST PARADIENE 20/30 FR | 1998-08-01 | UNKNOWN | 28 | 5 | 0 | 0 | 0 | 0 | 3 | 0 | 13 | 20 | -8
220 | O'Keeffe | R21 | R21 | 00R | ROOF | ROOF | 7246 | SIPLAST PARADIENE 20/30 FR | 1998-08-01 | METAL | 28 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -8
220 | O'Keeffe | R22 | R22 | 00R | ROOF | ROOF | 662 | SIPLAST PARADIENE 20/30 FR | 1998-08-01 | METAL | 28 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -8
78420

## X225_R
Location Number | Location | Roof Identification Number | School Number | Level | Area Name | Roof Type | Area (Sq. Ft.) | Roof Type | Date Installed | Deck Information | Age (Years) | Drainage 0-Good Slope/No Ponding 3-Low Slope/Some Ponding 5-Poor Slope/Ponding | Blisters 0-No Blisters 3-Less Than 20 Percent 5-More Than 20 Percent | Linear Folds/Cracks 0-No Folds/Cracks 3-Less Than 20 Percent 5-More Than 20 Percent | Flashing Condition 0-Good 3-Some Splits/Cracks 5-Poor Splits/Cracks Common | Leakage Problems 0-No leaks 3-Minor Leaks 5-Major Leaks | Surface Wear 0-No Wear Noted 3-Average Wear Noted 5-Excessive Wear Noted | Deck 0-Concrete 3-Metal 5-Wood | Total Score Condition | Estimated Service Life | Estimated Remaining Life
225 | Toki | C01 | C01 | 00R | CANOPY | CANOPY | 133 | UNKNOWN | 1962-08-01 | UNKNOWN | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | -49
225 | Toki | C02 | C02 | 00R | CANOPY | CANOPY | 24 | UNKNOWN | 1962-08-01 | UNKNOWN | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | -49
225 | Toki | C03 | C03 | 00R | CANOPY | CANOPY | 40 | SIPLAST PARADIENE 20/30 FR | 1999-08-01 | METAL | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -7
225 | Toki | R01 | R01 | 00R | ROOF | ROOF | 4788 | SIPLAST PARADIENE 20/30 FR | 2003-08-01 | METAL | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -3
225 | Toki | R02 | R02 | 00R | ROOF | ROOF | 10335 | SIPLAST PARADIENE 20/30 FR | 1999-08-01 | METAL | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -7
225 | Toki | R03 | R03 | 00R | ROOF | ROOF | 11678 | SIPLAST PARADIENE 20/30 FR | 1997-08-01 | METAL | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -9
225 | Toki | R04 | R04 | 00R | ROOF | TRACTOR STORAGE | 144 | SIPLAST PARADIENE 20/30 FR | 1997-08-01 | METAL | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -9
225 | Toki | R06 | R06 | 00R | ROOF | ROOF | 4812 | SIPLAST PARADIENE 20/30 FR | 2003-08-01 | METAL | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -3
225 | Toki | R07 | R07 | 00R | ROOF | ROOF | 5165 | TARMAC SBS FR | 1992-08-01 | METAL | 34 | 5 | 3 | 3 | 3 | 5 | 3 | 3 | 56 | 20 | -14
225 | Toki | R08 | R08 | 00R | ROOF | ROOF | 488 | TARMAC SBS FR | 1992-08-01 | METAL | 34 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -14
225 | Toki | R09 | R09 | 00R | ROOF | ROOF | 5042 | MANVILLE DYNAKAP FR | 1989-08-01 | METAL | 37 | 3 | 3 | 0 | 3 | 0 | 3 | 0 | 15 | 20 | -17
225 | Toki | R10 | R10 | 00R | ROOF | ROOF | 3279 | MANVILLE DYNAKAP FR | 1989-08-01 | METAL | 37 | 3 | 3 | 3 | 3 | 0 | 3 | 0 | 21 | 20 | -17
225 | Toki | R11 | R11 | 00R | ROOF | ROOF | 4935 | MANVILLE DYNAKAP FR | 1989-08-01 | METAL | 37 | 5 | 5 | 3 | 3 | 0 | 3 | 0 | 27 | 20 | -17
225 | Toki | R12 | R12 | 00R | ROOF | ROOF | 4388 | MANVILLE DYNAKAP FR | 1989-08-01 | METAL | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -17
225 | Toki | R13 | R13 | 00R | ROOF | ROOF | 12781 | TARMAC SBS FR | 1992-08-01 | METAL | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14
225 | Toki | R14 | R14 | 00R | ROOF | ROOF | 6452 | TARMAC SBS FR | 1992-08-01 | METAL | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14
225 | Toki | R15 | R15 | 00R | ROOF | ROOF | 486 | SIPLAST PARADIENE 20/30 FR | 1997-08-01 | METAL | 29 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 5 | 20 | -9
225 | Toki | R16 | R16 | 00R | ROOF | RELOCATABLE ROOF | 1611 | ASPHALT ROLLED ROOFING | 1962-08-01 | WOOD | 64 | 5 | 0 | 0 | 5 | 3 | 3 | 5 | 43 | 20 | -44
225 | Toki | R17 | R17 | 00R | ROOF | ROOF | 7182 | SIPLAST PARADIENE 20/30 FR | 1997-08-01 | METAL | 29 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 20 | -9
225 | Toki | R18 | R18 | 00R | ROOF | ROOF | 12545 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | METAL | 24 | 3 | 5 | 3 | 3 | 0 | 0 | 0 | 20 | 20 | -4
225 | Toki | R19 | R19 | 00R | ROOF | ROOF | 9969 | SIPLAST PARADIENE 20/30 FR | 1999-08-01 | METAL | 27 | 0 | 5 | 3 | 0 | 0 | 3 | 0 | 14 | 20 | -7
106277

## X227_r
Location Number | Location | Roof Identification Number | School Number | Level | Area Name | Roof Type | Area (Sq. Ft.) | Roof Type | Date Installed | Deck Information | Age (Years) | Drainage 0-Good Slope/No Ponding 3-Low Slope/Some Ponding 5-Poor Slope/Ponding | Blisters 0-No Blisters 3-Less Than 20 Percent 5-More Than 20 Percent | Linear Folds/Cracks 0-No Folds/Cracks 3-Less Than 20 Percent 5-More Than 20 Percent | Flashing Condition 0-Good 3-Some Splits/Cracks 5-Poor Splits/Cracks Common | Leakage Problems 0-No leaks 3-Minor Leaks 5-Major Leaks | Surface Wear 0-No Wear Noted 3-Average Wear Noted 5-Excessive Wear Noted | Deck 0-Concrete 3-Metal 5-Wood | Total Score Condition | Estimated Service Life | Estimated Remaining Life
227 | Whitehorse | R01 | R01 | 00R | ROOF | ROOF | 15114 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4
227 | Whitehorse | R02 | R02 | 00R | ROOF | ROOF | 2594 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4
227 | Whitehorse | R03 | R03 | 00R | ROOF | ROOF | 11717 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4
227 | Whitehorse | R04 | R04 | 00R | ROOF | ROOF | 4054 | TARMAC SBS FR | 1992-08-01 | METAL | 34 | 3 | 5 | 0 | 0 | 3 | 3 | 3 | 35 | 20 | -14
227 | Whitehorse | R05 | R05 | 00R | ROOF | ROOF | 5495 | TARMAC SBS FR | 1992-08-01 | METAL | 34 | 3 | 3 | 0 | 0 | 3 | 3 | 3 | 33 | 20 | -14
227 | Whitehorse | R06 | R06 | 00R | ROOF | ROOF | 4977 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4
227 | Whitehorse | R07 | R07 | 00R | ROOF | ROOF | 1877 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4
227 | Whitehorse | R08 | R08 | 00R | ROOF | ROOF | 208 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4
227 | Whitehorse | R09 | R09 | 00R | ROOF | ROOF | 3746 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4
227 | Whitehorse | R10 | R10 | 00R | ROOF | ROOF | 2006 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4
227 | Whitehorse | R11 | R11 | 00R | ROOF | ROOF | 12955 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4
227 | Whitehorse | R12 | R12 | 00R | ROOF | ROOF | 12966 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4
227 | Whitehorse | R13 | R13 | 00R | ROOF | ROOF | 14315 | TAMKO VERSA CAP FR 2-PLY | 1995-08-01 | METAL | 31 | 3 | 5 | 3 | 3 | 3 | 3 | 3 | 44 | 20 | -11
227 | Whitehorse | R14 | R14 | 00R | ROOF | ROOF | 13183 | UNKNOWN | 1989-08-01 | METAL | 37 | 3 | 5 | 0 | 0 | 3 | 3 | 3 | 35 | 15 | -22
227 | Whitehorse | R15 | R15 | 00R | ROOF | ROOF | 4997 | TAMKO VERSA CAP FR 2-PLY | 1995-08-01 | METAL | 31 | 0 | 3 | 0 | 3 | 3 | 3 | 3 | 30 | 20 | -11
110204

## R228_R
Location Number | Location | Roof Identification Number | School Number | Level | Area Name | Roof Type | Area (Sq. Ft.) | Roof Type | Date Installed | Deck Information | Age (Years) | Drainage 0-Good Slope/No Ponding 3-Low Slope/Some Ponding 5-Poor Slope/Ponding | Blisters 0-No Blisters 3-Less Than 20 Percent 5-More Than 20 Percent | Linear Folds/Cracks 0-No Folds/Cracks 3-Less Than 20 Percent 5-More Than 20 Percent | Flashing Condition 0-Good 3-Some Splits/Cracks 5-Poor Splits/Cracks Common | Leakage Problems 0-No leaks 3-Minor Leaks 5-Major Leaks | Surface Wear 0-No Wear Noted 3-Average Wear Noted 5-Excessive Wear Noted | Deck 0-Concrete 3-Metal 5-Wood | Total Score Condition | Estimated Service Life | Estimated Remaining Life
228 | Sherman | C01 | C01 | 00R | CANOPY | CANOPY | 122 | COAL TAR | 1960-08-01 | WOOD | 66 | 0 | 5 | 0 | 3 | 0 | 5 | 0 | 13 | 20 | -46
228 | Sherman | C02 | C02 | 00R | CANOPY | CANOPY | 128 | COAL TAR | 1960-08-01 | WOOD | 66 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 8 | 20 | -46
228 | Sherman | R01 | R01 | 00R | ROOF | ROOF | 9931 | TEMPORARY ROOF | 1996-08-01 | METAL | 30 | 0 | 5 | 1 | 3 | 0 | 3 | 0 | 13 | 7 | -23
228 | Sherman | R02 | R02 | 00R | ROOF | ROOF | 796 | SIPLAST PARADIENE 20/30 FR | 2003-08-03 | METAL | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -3
228 | Sherman | R02A | R02A | 00R | ELEVATOR ROOF | ROOF | 622 | SIPLAST PARADIENE 20/30 FR | 2003-08-01 | METAL | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -3
228 | Sherman | R03 | R03 | 00R | ROOF | ROOF | 160 | SIPLAST PARADIENE 20/30 FR | 2003-08-03 | METAL | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -3
228 | Sherman | R04 | R04 | 00R | ROOF | ROOF | 7434 | FIRESTONE-(MECH-FASTENED) | 1994-08-01 | WOOD | 32 | 3 | 0 | 0 | 0 | 3 | 0 | 5 | 31 | 15 | -17
228 | Sherman | R05 | R05 | 00R | ROOF | ROOF | 423 | SIPLAST PARADIENE 20/30 FR | 1993-08-01 | METAL | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -13
228 | Sherman | R06 | R06 | 00R | ROOF | ROOF | 1956 | SIPLAST PARADIENE 20/30 FR | 1993-08-01 | METAL | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -13
228 | Sherman | R07 | R07 | 00R | ROOF | ROOF | 4904 | SIPLAST PARADIENE 20/30 FR | 1993-08-01 | METAL | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -13
228 | Sherman | R08 | R08 | 00R | ROOF | ROOF | 1205 | SIPLAST PARADIENE 20/30 FR | 1993-08-01 | METAL | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -13
228 | Sherman | R09 | R09 | 00R | ROOF | ROOF | 48 | SIPLAST PARADIENE 20/30 FR | 1993-08-01 | METAL | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -13
228 | Sherman | R10 | R10 | 00R | ROOF | ROOF | 718 | SIPLAST PARADIENE 20/30 FR | 1993-08-01 | METAL | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -13
228 | Sherman | R11 | R11 | 00R | ROOF | ROOF | 4835 | SIPLAST PARADIENE 20/30 FR | 1993-08-01 | METAL | 33 | 3 | 3 | 0 | 0 | 0 | 0 | 0 | 9 | 20 | -13
228 | Sherman | R12 | R12 | 00R | ROOF | ROOF | 704 | SIPLAST PARADIENE 20/30 FR | 1993-08-01 | METAL | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -13
228 | Sherman | R13 | R13 | 00R | ROOF | ROOF | 7480 | SIPLAST PARADIENE 20/30 FR | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5
228 | Sherman | R14 | R14 | 00R | ROOF | ROOF | 5662 | MANVILLE DYNAGLAS FR | 1995-08-01 | METAL | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -11
228 | Sherman | R15 | R15 | 00R | ROOF | ROOF | 1815 | SIPLAST PARADIENE 20/30 FR | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5
228 | Sherman | R16 | R16 | 00R | ROOF | ROOF | 7923 | SIPLAST PARADIENE 20/30 FR | 2001-08-01 | CONCRETE | 25 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 20 | -5
228 | Sherman | R17 | R17 | 00R | ROOF | ROOF | 160 | SIPLAST PARADIENE 20/30 FR | 1993-08-01 | METAL | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -13
228 | Sherman | R18 | R18 | 00R | ELEVATOR ROOF | ROOF | 82 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4
228 | Sherman | R19 | R19 | 00R | ROOF | ROOF | 13216 | MODIFIED BIT. | 1996-08-01 | WOOD | 30 | 3 | 3 | 3 | 0 | 0 | 0 | 0 | 15 | 20 | -10
228 | Sherman | R20 | R20 | 00R | LMC ROOF | ROOF | 7013 | BUR 4-PLY | 1992-08-01 | WOOD | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14
77337

## X231_r
Location Number | Location | Roof Identification Number | School Number | Level | Area Name | Roof Type | Area (Sq. Ft.) | Roof Type | Date Installed | Deck Information | Age (Years) | Drainage 0-Good Slope/No Ponding 3-Low Slope/Some Ponding 5-Poor Slope/Ponding | Blisters 0-No Blisters 3-Less Than 20 Percent 5-More Than 20 Percent | Linear Folds/Cracks 0-No Folds/Cracks 3-Less Than 20 Percent 5-More Than 20 Percent | Flashing Condition 0-Good 3-Some Splits/Cracks 5-Poor Splits/Cracks Common | Leakage Problems 0-No leaks 3-Minor Leaks 5-Major Leaks | Surface Wear 0-No Wear Noted 3-Average Wear Noted 5-Excessive Wear Noted | Deck 0-Concrete 3-Metal 5-Wood | Total Score Condition | Estimated Service Life | Estimated Remaining Life
231 | Spring Harbor | C01 | C01 | 00R | CANOPY ROOF | ROOF | 508 | MANVILLE GLASPLY-IV 4-PLY | 1987-08-01 | METAL | 39 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 6 | 20 | -19
231 | Spring Harbor | R01 | R01 | 00R | ROOF | ROOF | 9182 | MANVILLE GLASPLY-IV 4-PLY | 1987-08-01 | METAL | 39 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 6 | 20 | -19
231 | Spring Harbor | R02 | R02 | 00R | ROOF | ROOF | 11482 | MANVILLE GLASPLY-IV 4-PLY | 1987-08-01 | METAL | 39 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 6 | 20 | -19
231 | Spring Harbor | R03 | R03 | 00R | LMC ROOF | ROOF | 4489 | MANVILLE GLASPLY-IV 4-PLY | 1987-08-01 | METAL | 39 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 6 | 20 | -19
231 | Spring Harbor | R04 | R04 | 00R | GYMNASIUM ROOF | ROOF | 5201 | MANVILLE GLASPLY-IV 4-PLY | 1987-08-01 | METAL | 39 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 6 | 20 | -19
30862

## R234_R
Location Number | Location | Roof Identification Number | School Number | Level | Area Name | Roof Type | Area (Sq. Ft.) | Roof Type | Date Installed | Deck Information | Age (Years) | Drainage 0-Good Slope/No Ponding 3-Low Slope/Some Ponding 5-Poor Slope/Ponding | Blisters 0-No Blisters 3-Less Than 20 Percent 5-More Than 20 Percent | Linear Folds/Cracks 0-No Folds/Cracks 3-Less Than 20 Percent 5-More Than 20 Percent | Flashing Condition 0-Good 3-Some Splits/Cracks 5-Poor Splits/Cracks Common | Leakage Problems 0-No leaks 3-Minor Leaks 5-Major Leaks | Surface Wear 0-No Wear Noted 3-Average Wear Noted 5-Excessive Wear Noted | Deck 0-Concrete 3-Metal 5-Wood | Total Score Condition | Estimated Service Life | Estimated Remaining Life
234 | Hamilton | C01 | C01 | 00R | CANOPY | CANOPY | 89 | SIPLAST PARADIENE 20/30 FR | 2000-08-01 | METAL | 26 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -6
234 | Hamilton | R01 | R01 | 00R | ROOF | LMC ROOF | 5480 | GAF GAFGLAS 4-PLY W/GRAV | 1991-08-01 | WOOD | 35 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | 20 | -15
234 | Hamilton | R02 | R02 | 00R | ROOF | ROOF | 18570 | SIPLAST PARADIENE 20/30 FR | 2000-08-01 | WOOD | 26 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | 20 | -6
234 | Hamilton | R03 | R03 | 00R | ROOF | ROOF | 4488 | SIPLAST PARADIENE 20/30 FR | 2000-08-01 | WOOD | 26 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | 20 | -6
234 | Hamilton | R04 | R04 | 00R | ROOF | ROOF | 611 | SIPLAST COVER | 1997-08-01 | METAL | 29 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 7 | -22
234 | Hamilton | R05 | R05 | 00R | ROOF | ROOF | 12150 | SCHULER 3FID MODIFIED | 1995-08-01 | WOOD | 31 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | 20 | -11
234 | Hamilton | R06 | R06 | 00R | ROOF | ROOF | 1204 | SIPLAST PARADIENE 20/30 FR | 2000-08-01 | METAL | 26 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -6
234 | Hamilton | R07 | R07 | 00R | ROOF | ROOF | 1876 | SIPLAST PARADIENE 20/30 FR | 2000-08-01 | METAL | 26 | 0 | 0 | 0 | 0 | 3 | 3 | 3 | 24 | 20 | -6
234 | Hamilton | R08 | R08 | 00R | ROOF | ROOF | 2013 | SIPLAST PARADIENE 20/30 FR | 1989-08-01 | METAL | 37 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -17
234 | Hamilton | R09 | R09 | 00R | ROOF | ROOF | 1667 | SIPLAST PARADIENE 20/30 FR | 2000-08-01 | METAL | 26 | 0 | 0 | 0 | 0 | 3 | 3 | 3 | 24 | 20 | -6
234 | Hamilton | R10 | R10 | 00R | ROOF | ROOF | 214 | SIPLAST PARADIENE 20/30 FR | 1989-08-01 | METAL | 37 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -17
234 | Hamilton | R11 | R11 | 00R | ROOF | ROOF | 772 | SIPLAST PARADIENE 20/30 FR | 1989-08-01 | METAL | 37 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -17
234 | Hamilton | R12 | R12 | 00R | ROOF | ROOF | 7338 | SIPLAST PARADIENE 20/30 FR | 1989-08-01 | ACOUSTICAL-METAL | 37 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -17
234 | Hamilton | R13 | R13 | 00R | ROOF | ROOF | 770 | SIPLAST PARADIENE 20/30 FR | 1989-08-01 | METAL | 37 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -17
234 | Hamilton | R14 | R14 | 00R | ROOF | ROOF | 1416 | SIPLAST PARADIENE 20/30 FR | 1989-08-01 | METAL | 37 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -17
234 | Hamilton | R15 | R15 | 00R | ROOF | ROOF | 217 | SIPLAST PARADIENE 20/30 FR | 1991-08-01 | METAL | 35 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -15
234 | Hamilton | R16 | R16 | 00R | ROOF | ROOF | 1021 | SIPLAST PARADIENE 20/30 FR | 2000-08-01 | METAL | 26 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -6
234 | Hamilton | R25 | R25 | 00R | ROOF | ROOF | 14560 | MANVILLE GLASPLY-IV 4-PLY | 1988-08-01 | WOOD | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -18
234 | Hamilton | R17 | R17 | 00R | ROOF | ROOF | 7366 | SIPLAST PARADIENE 20/30 FR | 1988-08-01 | METAL | 38 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 9 | 20 | -18
234 | Hamilton | R18 | R18 | 00R | ROOF | ROOF | 2780 | SIPLAST PARADIENE 20/30 FR | 1988-08-01 | METAL | 38 | 3 | 3 | 0 | 0 | 3 | 3 | 3 | 33 | 20 | -18
234 | Hamilton | R19 | R19 | 00R | ROOF | ROOF | 2812 | SIPLAST PARADIENE 20/30 FR | 1988-08-01 | METAL | 38 | 3 | 3 | 0 | 0 | 0 | 3 | 0 | 12 | 20 | -18
234 | Hamilton | R20 | R20 | 00R | ROOF | ROOF | 1306 | SIPLAST PARADIENE 20/30 FR | 2000-08-01 | METAL | 26 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -6
234 | Hamilton | R21 | R21 | 00R | ROOF | ROOF | 4021 | SIPLAST PARADIENE 20/30 FR | 2000-08-01 | METAL | 26 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -6
234 | Hamilton | R22 | R22 | 00R | ROOF | ROOF | 2130 | MANVILLE GLASPLY-IV 4-PLY | 1988-08-01 | WOOD | 38 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 6 | 20 | -18
234 | Hamilton | R23 | R23 | 00R | ROOF | ROOF | 14277 | MANVILLE GLASPLY-IV 4-PLY | 1988-08-01 | WOOD | 38 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | 20 | -18
234 | Hamilton | R24 | R24 | 00R | ROOF | ROOF | 1228 | BUR 4-PLY | 1962-08-01 | WOOD | 64 | 3 | 0 | 0 | 3 | 3 | 5 | 5 | 39 | 20 | -44

## X239_R
Location Number | Location | Roof Identification Number | School Number | Level | Area Name | Roof Type | Area (Sq. Ft.) | Roof Type | Date Installed | Deck Information | Age (Years) | Drainage 0-Good Slope/No Ponding 3-Low Slope/Some Ponding 5-Poor Slope/Ponding | Blisters 0-No Blisters 3-Less Than 20 Percent 5-More Than 20 Percent | Linear Folds/Cracks 0-No Folds/Cracks 3-Less Than 20 Percent 5-More Than 20 Percent | Flashing Condition 0-Good 3-Some Splits/Cracks 5-Poor Splits/Cracks Common | Leakage Problems 0-No leaks 3-Minor Leaks 5-Major Leaks | Surface Wear 0-No Wear Noted 3-Average Wear Noted 5-Excessive Wear Noted | Deck 0-Concrete 3-Metal 5-Wood | Total Score Condition | Estimated Service Life | Estimated Remaining Life
239 | Wright | C01 | C01 | 00R | ENTRANCE CANOPY | ROOF | 807 | SIPLAST PARADIENE 20/30 FR | 1997-08-01 | METAL | 29 | 0 | 3 | 0 | 0 | 3 | 3 | 3 | 27 | 20 | -9
239 | Wright | R01 | R01 | 00R | ROOF | ROOF | 557 | SIPLAST PARADIENE 20/30 FR | 1997-08-01 | METAL | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -9
239 | Wright | R02 | R02 | 00R | ROOF | ROOF | 16398 | SIPLAST PARADIENE 20/30 FR | 1997-08-01 | METAL | 29 | 0 | 3 | 2 | 0 | 3 | 3 | 3 | 31 | 20 | -9
239 | Wright | R03 | R03 | 00R | ROOF | ROOF | 2649 | SIPLAST PARADIENE 20/30 FR | 1997-08-01 | METAL | 29 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 20 | -9
239 | Wright | R04 | R04 | 00R | ROOF | ROOF | 1596 | SIPLAST PARADIENE 20/30 FR | 1997-08-01 | METAL | 29 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 20 | -9
239 | Wright | R05 | R05 | 00R | ROOF | ROOF | 10625 | SIPLAST PARADIENE 20/30 FR | 1997-08-01 | METAL | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -9
239 | Wright | R06 | R06 | 00R | ROOF | ROOF | 1237 | SIPLAST PARADIENE 20/30 FR | 1997-08-01 | METAL | 29 | 0 | 0 | 0 | 0 | 3 | 1 | 3 | 22 | 20 | -9

## R242_r
Location Number | Location | Roof Identification Number | School Number | Level | Area Name | Roof Type | Area (Sq. Ft.) | Roof Type | Date Installed | Deck Information | Age (Years) | Drainage 0-Good Slope/No Ponding 3-Low Slope/Some Ponding 5-Poor Slope/Ponding | Blisters 0-No Blisters 3-Less Than 20 Percent 5-More Than 20 Percent | Linear Folds/Cracks 0-No Folds/Cracks 3-Less Than 20 Percent 5-More Than 20 Percent | Flashing Condition 0-Good 3-Some Splits/Cracks 5-Poor Splits/Cracks Common | Leakage Problems 0-No leaks 3-Minor Leaks 5-Major Leaks | Surface Wear 0-No Wear Noted 3-Average Wear Noted 5-Excessive Wear Noted | Deck 0-Concrete 3-Metal 5-Wood | Total Score Condition | Estimated Service Life | Estimated Remaining Life
242 | Sennett | C01 | C01 | 00R | Main Entrance Canopy | Canopy | 153 | MANVILLE DYNAKAP FR,2.2" | 1989-08-01 | STEEL/CONCRETE | 37 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -17
242 | Sennett | C02 | C02 | 00R | Rear Entrance | Canopy | 158 | MANVILLE DYNAKAP FR,2.2" | 1989-08-01 | STEEL/CONCRETE | 37 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -17
242 | Sennett | R01 | R01 | 00R | Old Cafeteria | ROOF | 875 | BUR 4-PLY | 1980-08-01 | METAL | 46 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -26
242 | Sennett | R02 | R02 | 00R | GYM NW AREA | ROOF | 1575 | MANVILLE DYNAKAP FR,2.2" | 1989-08-01 | STEEL/CONCRETE | 37 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 6 | 20 | -17
242 | Sennett | R03 | R03 | 00R | GYM ROOF SW | ROOF | 1573 | MANVILLE DYNAKAP FR,2.2" | 1989-08-01 | STEEL/CONCRETE | 37 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | -17
242 | Sennett | R04 | R04 | 00R | GYM ROOF NE | ROOF | 1584 | MANVILLE DYNAKAP FR, 2.2" | 1989-08-01 | STEEL/CONCRETE | 37 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | -17
242 | Sennett | R05 | R05 | 00R | GYM ROOF SE | ROOF | 1583 | MANVILLE DYNAKAP FR,2.2" | 1989-08-01 | STEEL/CONCRETE | 37 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | -17
242 | Sennett | R06 | R06 | 00R | UPPER MECH NORTH | ROOF | 1413 | MANVILLE DYNAKAP FR,2.2" | 1989-08-01 | STEEL/CONCRETE | 37 | 3 | 3 | 0 | 3 | 0 | 3 | 0 | 15 | 20 | -17
242 | Sennett | R07 | R07 | 00R | UPPER MECH SOUTH | ROOF | 1406 | MANVILLE DYNAKAP FR,2.2" | 1989-08-01 | STEEL/CONCRETE | 37 | 3 | 3 | 3 | 3 | 0 | 3 | 0 | 21 | 20 | -17
242 | Sennett | R08 | R08 | 00R | CLASSROOM NW | ROOF | 2763 | MANVILLE DYNAKAP FR,2.2" | 1989-08-01 | STEEL/CONCRETE | 37 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | -17
242 | Sennett | R09 | R09 | 00R | ROOF | ROOF | 2293 | MANVILLE DYNAKAP FR,2.2" | 1989-08-01 | STEEL/CONCRETE | 37 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | -17
242 | Sennett | R10 | R10 | 00R | ROOF | ROOF | 2744 | MANVILLE DYNAKAP FR, 2.2" | 1989-08-01 | STEEL/CONCRETE | 37 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | -17
242 | Sennett | R11 | R11 | 00R | ROOF | ROOF | 2634 | MANVILLE DYNAKAP FR,2.2" | 1989-08-01 | STEEL/CONCRETE | 37 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 6 | 20 | -17
242 | Sennett | R12 | R12 | 00R | ROOF | ROOF | 2210 | MANVILLE DYNAKAP FR,2.2" | 1989-08-01 | STEEL/CONCRETE | 37 | 3 | 3 | 0 | 3 | 0 | 3 | 0 | 15 | 20 | -17
242 | Sennett | R13 | R13 | 00R | ROOF | ROOF | 2617 | MANVILLE DYNAKAP FR,2.2" | 1989-08-01 | STEEL/CONCRETE | 37 | 3 | 3 | 0 | 3 | 0 | 3 | 0 | 15 | 20 | -17
242 | Sennett | R14 | R14 | 00R | ROOF | ROOF | 2713 | MANVILLE DYNAKAP FR, 2.2" | 1989-08-01 | STEEL/CONCRETE | 37 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | -17
242 | Sennett | R15 | R15 | 00R | ROOF | ROOF | 2243 | MANVILLE DYNAKAP FR, 2.2" | 1989-08-01 | STEEL/CONCRETE | 37 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 6 | 20 | -17
242 | Sennett | R16 | R16 | 00R | ROOF | ROOF | 2691 | MANVILLE DYNAKAP FR,2.2" | 1989-08-01 | STEEL/CONCRETE | 37 | 0 | 5 | 0 | 3 | 0 | 3 | 0 | 11 | 20 | -17
242 | Sennett | R17 | R17 | 00R | ROOF | ROOF | 2708 | MANVILLE DYNAKAP FR,2.2" | 1989-08-01 | STEEL/CONCRETE | 37 | 0 | 3 | 0 | 3 | 3 | 3 | 3 | 30 | 20 | -17
242 | Sennett | R18 | R18 | 00R | ROOF | ROOF | 2250 | MANVILLE DYNAKAP FR, 2.2" | 1989-08-01 | STEEL/CONCRETE | 37 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 6 | 20 | -17
242 | Sennett | R19 | R19 | 00R | ROOF | ROOF | 2676 | MANVILLE DYNAKAP FR,2.2" | 1989-08-01 | STEEL/CONCRETE | 37 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | -17
242 | Sennett | R20 | R20 | 00R | ROOF | ROOF | 1276 | MANVILLE DYNAKAP FR, 2.2" | 1989-08-01 | STEEL/CONCRETE | 37 | 3 | 3 | 0 | 3 | 0 | 3 | 0 | 15 | 20 | -17
242 | Sennett | R21 | R21 | 00R | ROOF | ROOF | 2917 | MANVILLE DYNAGLAS DYNABAS | 1992-08-01 | METAL | 34 | 0 | 5 | 0 | 3 | 0 | 3 | 0 | 11 | 20 | -14
242 | Sennett | R22 | R22 | 00R | ROOF | ROOF | 3050 | MANVILLE DYNAGLAS DYNABAS | 1992-08-01 | METAL | 34 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | -14
242 | Sennett | R23 | R23 | 00R | ROOF | ROOF | 3067 | MANVILLE DYNAGLAS DYNABAS | 1992-08-01 | METAL | 34 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | -14
242 | Sennett | R24 | R24 | 00R | ROOF | ROOF | 2879 | MANVILLE DYNAGLAS DYNABAS | 1992-08-01 | METAL | 34 | 0 | 3 | 3 | 3 | 0 | 3 | 0 | 15 | 20 | -14
54051

## X245_r
Location Number | Location | Roof Identification Number | School Number | Level | Area Name | Roof Type | Area (Sq. Ft.) | Roof Type | Date Installed | Deck Information | Age (Years) | Drainage 0-Good Slope/No Ponding 3-Low Slope/Some Ponding 5-Poor Slope/Ponding | Blisters 0-No Blisters 3-Less Than 20 Percent 5-More Than 20 Percent | Linear Folds/Cracks 0-No Folds/Cracks 3-Less Than 20 Percent 5-More Than 20 Percent | Flashing Condition 0-Good 3-Some Splits/Cracks 5-Poor Splits/Cracks Common | Leakage Problems 0-No leaks 3-Minor Leaks 5-Major Leaks | Surface Wear 0-No Wear Noted 3-Average Wear Noted 5-Excessive Wear Noted | Deck 0-Concrete 3-Metal 5-Wood | Total Score Condition | Estimated Service Life | Estimated Remaining Life
245 | Jefferson | R01 | R01 | 00R | ROOF | ROOF | 12411 | SIPLAST PARADIENE 20/30 FR | 1989-08-01 | METAL | 37 | 3 | 3 | 0 | 0 | 0 | 3 | 0 | 12 | 20 | -17
245 | Jefferson | R02 | R02 | 00R | ROOF | ROOF | 16841 | SIPLAST PARADIENE 20/30 FR | 1989-08-01 | METAL | 37 | 3 | 5 | 0 | 0 | 3 | 3 | 3 | 35 | 20 | -17
245 | Jefferson | R03 | R03 | 00R | ROOF | ROOF | 10511 | SIPLAST PARADIENE 20/30 FR | 1989-08-01 | METAL | 37 | 3 | 3 | 0 | 0 | 0 | 3 | 0 | 12 | 20 | -17
245 | Jefferson | R04 | R04 | 00R | ROOF | ROOF | 1849 | SIPLAST PARADIENE 20/30 FR | 1989-08-01 | METAL | 37 | 3 | 3 | 0 | 0 | 0 | 3 | 0 | 12 | 20 | -17
245 | Jefferson | R05 | R05 | 00R | ROOF | ROOF | 6698 | SIPLAST PARADIENE 20/30 FR | 1989-08-01 | METAL | 37 | 3 | 5 | 0 | 0 | 3 | 3 | 3 | 35 | 20 | -17
245 | Jefferson | R06 | R06 | 00R | ROOF | ROOF | 1876 | SIPLAST PARADIENE 20/30 FR | 1989-08-01 | METAL | 37 | 3 | 3 | 0 | 0 | 0 | 3 | 0 | 12 | 20 | -17
50186

## R141
Location Number | Location | Roof Identification Number | School Number | Level | Area Name | Roof Type | Area (Sq. Ft.) | Roof Type | Date Installed | Deck Information | Age (Years) | Drainage 0-Good Slope/No Ponding 3-Low Slope/Some Ponding 5-Poor Slope/Ponding | Blisters 0-No Blisters 3-Less Than 20 Percent 5-More Than 20 Percent | Linear Folds/Cracks 0-No Folds/Cracks 3-Less Than 20 Percent 5-More Than 20 Percent | Flashing Condition 0-Good 3-Some Splits/Cracks 5-Poor Splits/Cracks Common | Leakage Problems 0-No leaks 3-Minor Leaks 5-Major Leaks | Surface Wear 0-No Wear Noted 3-Average Wear Noted 5-Excessive Wear Noted | Deck 0-Concrete 3-Metal 5-Wood | Total Score Condition | Estimated Service Life | Estimated Remaining Life
141 | East | GRH1 | GRH1 | 00R | GREEN HOUSE | ROOF | 398 | ALUMINUM FRAME/GLASS | 1987-08-01 | NONE | 39 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 15 | 50 | 11
141 | East | GRH2 | GRH2 | 00R | GREEN HOUSE | ROOF | 398 | ALUMINUM FRAME/GLASS | 1995-08-01 | NONE | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 19
141 | East | P01 | P01 | 00R | PLAZA | PLAZA - LOCKER RM AREA | 9776 | CONCRETE/MEMBRANE | 1970-08-01 | CONCRETE | 56 | 5 | 0 | 0 | 3 | 5 | 3 | 0 | 41 | 35 | -21
141 | East | P02 | P02 | 00R | PLAZA | PLAZA - COOLING TOWER ARE | 829 | CONCRETE PAVERS/MEMBRANE | 1970-08-01 | CONCRETE | 56 | 5 | 0 | 0 | 3 | 0 | 0 | 0 | 13 | 35 | -21
141 | East | PH1 | PH1 | 00R | ROOF | PENTHOUSE ROOF | 1228 | SIPLAST PARADIENE 20/30 FR | 1965-08-01 | UNKNOWN | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -41
141 | East | PH2 | PH2 | 00R | ROOF | PENTHOUSE ROOF | 984 | MODIFIED BIT. | 1965-08-01 | UNKNOWN | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -41
141 | East | PH3 | PH3 | 00R | ROOF | PENTHOUSE ROOF | 830 | SCHULLER 2FID MODIFIED | 1996-08-01 | METAL | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -10
141 | East | PH4 | PH4 | 00R | ROOF | PENTHOUSE ROOF | 830 | SCHULLER 2FID MODIFIED | 1996-08-01 | METAL | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -10
141 | East | PH5 | PH5 | 00R | ROOF | PENTHOUSE ROOF | 863 | SIPLAST PARADIENE 20/30 FR | 2000-08-01 | METAL | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -6
141 | East | PH6 | PH6 | 00R | ROOF | PENTHOUSE ROOF | 863 | SIPLAST PARADIENE 20/30 FR | 2000-08-01 | METAL | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -6
141 | East | PH7 | PH7 | 00R | ROOF | PENTHOUSE ROOF | 219 | SIPLAST PARADIENE 20/30 FR | 2000-08-01 | METAL | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -6
141 | East | R01 | R01 | 00R | ROOF | FIELD HOUSE ROOF | 25931 | MANVILLE GLASPLY-IV 4-PLY | 1991-08-01 | METAL | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -15
141 | East | R02 | R02 | 00R | ROOF | ROOF | 299 | MANVILLE GLASPLY-IV 4-PLY | 1991-08-01 | METAL | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -15
141 | East | R04 | R04 | 00R | ROOF | ROOF | 222 | MANVILLE GLASPLY-IV 4-PLY | 1991-08-01 | METAL | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -15
141 | East | R05 | R05 | 00R | ROOF | ROOF | 23216 | SIPLAST PARADIENE 20/30 FR | 2000-08-01 | CONCRETE | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -6
141 | East | R5A | R5A | 00R | ROOF | ROOF | 172 | SIPLAST PARADIENE 20/30 FR | 2000-08-01 | CONCRETE | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -6
141 | East | R5B | R5B | 00R | ROOF | ROOF | 172 | SIPLAST PARADIENE 20/30 FR | 2000-08-01 | CONCRETE | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -6
141 | East | R06 | R06 | 00R | ROOF | ROOF | 3937 | MANVILLE DYNAGLAS FR | 1995-08-01 | METAL | 31 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 6 | 20 | -11
141 | East | R07 | R07 | 00R | ROOF | ROOF | 5372 | MANVILLE DYNAGLAS FR | 1995-08-01 | METAL | 31 | 0 | 3 | 0 | 3 | 3 | 3 | 3 | 30 | 20 | -11
141 | East | R08 | R08 | 00R | ROOF | ROOF | 2323 | SCHULLER 3FID MODIFIED | 1995-08-01 | METAL | 31 | 0 | 5 | 0 | 3 | 0 | 3 | 0 | 11 | 20 | -11
141 | East | R09 | R09 | 00R | ROOF | ROOF | 477 | SCHULLER 3FID MODIFIED | 1995-08-01 | METAL | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -11
141 | East | R10 | R10 | 00R | ROOF | ROOF | 1832 | SCHULLER 3FID MODIFIED | 1995-08-01 | METAL | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -11
141 | East | R11 | R11 | 00R | ROOF | ROOF | 478 | SCHULLER 3FID MODIFIED | 1995-08-01 | METAL | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -11
141 | East | R13 | R13 | 00R | ROOF | ROOF | 1926 | GRACE GRM 500 | 1986-08-01 | METAL | 40 | 3 | 0 | 0 | 3 | 5 | 3 | 3 | 43 | 15 | -25
141 | East | R14 | R14 | 00R | ROOF | ROOF | 4804 | BUR 4-PLY | 1965-08-01 | UNKNOWN | 61 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 20 | -41
141 | East | R15 | R15 | 00R | ROOF | ROOF | 317 | SCHULLER 3FID MODIFIED | 1995-08-01 | METAL | 31 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 6 | 20 | -11
141 | East | R16 | R16 | 00R | ROOF | ROOF | 612 | SCHULLER 3FID MODIFIED | 1995-08-01 | METAL | 31 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | -11
141 | East | R17 | R17 | 00R | ROOF | ROOF | 6579 | MANVILLE DYNAKAP FR, EXIS | 1987-08-01 | METAL | 39 | 5 | 3 | 3 | 3 | 0 | 3 | 0 | 25 | 20 | -19
141 | East | R17A | R17A | 00R | ROOF | ROOF | 359 | UNKNOWN | 1965-08-01 | UNKNOWN | 61 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 5 | 20 | -41
141 | East | R18 | R18 | 00R | ROOF | ROOF | 2840 | SCHULLER 3FID MODIFIED | 1995-08-01 | METAL | 31 | 0 | 0 | 3 | 3 | 0 | 3 | 0 | 12 | 20 | -11
141 | East | R18A | R18A | 00R | ROOF | ROOF | 361 | UNKNOWN | 1965-08-01 | UNKNOWN | 61 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 20 | -41
141 | East | R19 | R19 | 00R | ROOF | ROOF | 909 | SCHULLER 3FID MODIFIED | 1995-09-01 | METAL | 31 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 8 | 20 | -11
141 | East | R20 | R20 | 00R | ROOF | ROOF | 1646 | SCHULLER 3FID MODIFIED | 1995-08-01 | METAL | 31 | 0 | 3 | 3 | 3 | 0 | 3 | 0 | 15 | 20 | -11
141 | East | R21 | R21 | 00R | ROOF | ROOF | 1121 | SCHULLER 3FID MODIFIED | 1995-08-01 | METAL | 31 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | -11
141 | East | R22 | R22 | 00R | ROOF | ROOF | 1774 | SCHULLER 3FID MODIFIED | 1995-08-01 | METAL | 31 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | -11
141 | East | R23 | R23 | 00R | ROOF | ROOF | 12321 | SCHULLER 2FID MODIFIED | 1996-08-01 | CONCRETE | 30 | 3 | 3 | 0 | 3 | 0 | 3 | 0 | 15 | 20 | -10
141 | East | R24 | R24 | 00R | ROOF | ROOF | 11571 | GRACE GRM 500 | 1965-08-01 | METAL | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -41
141 | East | R25 | R25 | 00R | ROOF | ROOF | 1325 | SCHULLER 3FID MODIFIED | 1995-08-01 | METAL | 31 | 0 | 5 | 0 | 3 | 0 | 3 | 0 | 11 | 20 | -11
141 | East | R25A | R25A | 00R | ROOF | ROOF | 480 | SCHULLER 3FID MODIFIED | 1995-08-01 | METAL | 31 | 0 | 5 | 0 | 3 | 0 | 3 | 0 | 11 | 20 | -11
141 | East | R25B | R25B | 00R | ROOF | ROOF | 273 | SCHULLER 3FID MODIFIED | 1995-08-01 | METAL | 31 | 0 | 5 | 0 | 3 | 0 | 3 | 0 | 11 | 20 | -11
141 | East | R26 | R26 | 00R | ROOF | ROOF | 307 | CARLISLE SURE-SEAL EPDM 4 | 1981-08-01 | CONCRETE | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | -30
141 | East | R27 | R27 | 00R | ROOF | ROOF | 1539 | CARLISLE SURE-SEAL EPDM 4 | 1981-08-01 | CONCRETE | 45 | 0 | 0 | 0 | 5 | 0 | 3 | 0 | 8 | 15 | -30
141 | East | R28 | R28 | 00R | ROOF | ROOF | 320 | CARLISLE SURE-SEAL EPDM 4 | 1981-08-01 | CONCRETE | 45 | 0 | 0 | 0 | 5 | 0 | 3 | 0 | 8 | 15 | -30
141 | East | R29 | R29 | 00R | ROOF | ROOF | 1668 | MANVILLE DYNAKAP FR, ISO/ | 1987-08-01 | METAL | 39 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 6 | 20 | -19
141 | East | R30 | R30 | 00R | ROOF | ROOF | 1735 | MANVILLE DYNAKAP FR, ISO/ | 1987-08-01 | METAL | 39 | 0 | 5 | 0 | 3 | 0 | 3 | 0 | 11 | 20 | -19
141 | East | R31 | R31 | 00R | ROOF | ROOF | 8077 | ARMCO 24GA ALUMINIZED STE | 1981-08-01 | METAL | 45 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 3 | 25 | -20
141 | East | R32 | R32 | 00R | ROOF | ROOF | 1171 | MODIFIED BIT. | 1981-08-01 | METAL | 45 | 0 | 5 | 0 | 5 | 0 | 5 | 0 | 15 | 20 | -25
141 | East | R33 | R33 | 00R | ROOF | ROOF | 3836 | MANVILLE DYNAKAP FR, ISO/ | 1987-08-01 | METAL | 39 | 0 | 5 | 0 | 5 | 0 | 0 | 0 | 10 | 20 | -19
141 | East | R34 | R34 | 00R | ROOF | ROOF | 2862 | MANVILLE DYNAKAP FR, ISO/ | 1987-08-01 | CONCRETE | 39 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | -19
141 | East | R35 | R35 | 00R | ROOF | ROOF | 3302 | MANVILLE DYNAKAP FR, ISO/ | 1987-08-01 | CONCRETE | 39 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -19
141 | East | R36 | R36 | 00R | ROOF | ROOF | 987 | MANVILLE DYNAKAP FR, ISO/ | 1987-08-01 | CONCRETE | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -19
141 | East | R37 | R37 | 00R | ROOF | ROOF | 7846 | SCHULLER 2FID MODIFIED | 1996-08-01 | METAL | 30 | 3 | 3 | 0 | 3 | 0 | 3 | 0 | 15 | 20 | -10
141 | East | R38 | R38 | 00R | TOWER | ROOF | 529 | SCHULLER 2FID MODIFIED | 1996-08-01 | CONCRETE | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -10
141 | East | R39 | R39 | 00R | ROOF | ROOF | 12265 | MANVILLE DYNAKAP FR, ISO/ | 1987-08-01 | PRECAST CONCRETE | 39 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 20 | -19
141 | East | R40 | R40 | 00R | ROOF | ROOF | 14333 | MANVILLE DYNAKAP FR, ISO/ | 1987-08-01 | CONCRETE | 39 | 0 | 5 | 0 | 3 | 0 | 3 | 0 | 11 | 20 | -19
141 | East | R41 | R41 | 00R | ROOF | ROOF | 1190 | MANVILLE DYNAKAP FR, ISO/ | 1987-08-01 | CONCRETE | 39 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | -19
141 | East | R42 | R42 | 00R | ROOF | ROOF | 5595 | MANVILLE DYNAKAP FR, ISO/ | 1987-08-01 | PRECAST CONCRETE | 39 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | -19
198429

## R142_R
Location Number | Location | Roof Identification Number | School Number | Level | Area Name | Roof Type | Area (Sq. Ft.) | Roof Type | Date Installed | Deck Information | Age (Years) | Drainage 0-Good Slope/No Ponding 3-Low Slope/Some Ponding 5-Poor Slope/Ponding | Blisters 0-No Blisters 3-Less Than 20 Percent 5-More Than 20 Percent | Linear Folds/Cracks 0-No Folds/Cracks 3-Less Than 20 Percent 5-More Than 20 Percent | Flashing Condition 0-Good 3-Some Splits/Cracks 5-Poor Splits/Cracks Common | Leakage Problems 0-No leaks 3-Minor Leaks 5-Major Leaks | Surface Wear 0-No Wear Noted 3-Average Wear Noted 5-Excessive Wear Noted | Deck 0-Concrete 3-Metal 5-Wood | Total Score Condition | Estimated Service Life | Estimated Remaining Life
142 | LaFollette | R01 | R01 | 00R | ROOF | ROOF | 12277 | UNKNOWN | 1994-08-01 | METAL | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -12
142 | LaFollette | R02 | R02 | 00R | ROOF | ROOF | 304 | UNKNOWN | 1992-08-01 | METAL | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14
142 | LaFollette | R03 | R03 | 00R | ROOF | ROOF | 6102 | SIPLAST PARADIENE 20/30 FR | 1986-08-01 | METAL | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -20
142 | LaFollette | R04 | R04 | 00R | ROOF | ROOF | 5190 | MANVILLE GLASPLY-IV 4-PLY | 1993-08-01 | METAL | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -13
142 | LaFollette | R05 | R05 | 00R | ROOF | ROOF | 8232 | MANVILLE GLASPLY-IV 4-PLY | 1993-08-01 | METAL | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -13
142 | LaFollette | R06 | R06 | 00R | ROOF | ROOF | 5350 | MANVILLE GLASPLY-IV 4-PLY | 1993-08-01 | METAL | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -13
142 | LaFollette | R07 | R07 | 00R | ROOF | ROOF | 8032 | SCHULLER 2FID MODIFIED | 1996-08-01 | METAL | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -10
142 | LaFollette | R08 | R08 | 00R | ROOF | ROOF | 4154 | SCHULLER 2FID MODIFIED | 1996-08-01 | METAL | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -10
142 | LaFollette | R09 | R09 | 00R | ROOF | ROOF | 814 | SARNIFIL | 1992-08-01 | Concrete | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14
142 | LaFollette | R10 | R10 | 00R | ROOF | ROOF | 13724 | MANVILLE DYNAKAP FR | 1993-08-01 | METAL | 33 | 3 | 3 | 0 | 3 | 5 | 3 | 3 | 46 | 20 | -13
142 | LaFollette | R11 | R11 | 00R | ROOF | ROOF | 8368 | SCHULLER 2FID MODIFIED | 1996-08-01 | METAL | 30 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 20 | -10
142 | LaFollette | R12 | R12 | 00R | ROOF | ROOF | 3794 | SCHULLER 2FID MODIFIED | 1996-08-01 | METAL | 30 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 20 | -10
142 | LaFollette | R13 | R13 | 00R | ROOF | ROOF | 7280 | UNKNOWN | 1993-08-01 | METAL | 33 | 3 | 3 | 0 | 3 | 3 | 3 | 3 | 36 | 20 | -13
142 | LaFollette | R14 | R14 | 00R | ROOF | ROOF | 7267 | UNKNOWN | 1993-08-01 | METAL | 33 | 3 | 3 | 0 | 3 | 0 | 3 | 0 | 15 | 20 | -13
142 | LaFollette | R15 | R15 | 00R | ROOF | ROOF | 4628 | UNKNOWN | 1993-08-01 | METAL | 33 | 3 | 3 | 0 | 3 | 0 | 3 | 0 | 15 | 20 | -13
142 | LaFollette | R16 | R16 | 00R | ROOF | ROOF | 7495 | UNKNOWN | 1965-08-01 | METAL | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -41
142 | LaFollette | R17 | R17 | 00R | ROOF | ROOF | 9677 | SIPLAST PARADIENE 20/30 FR | 1992-08-01 | METAL | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14
142 | LaFollette | R17A | R17A | 00R | ROOF | ROOF | 2782 | UNKNOWN | 1992-08-01 | METAL | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14
142 | LaFollette | R17B | R17B | 00R | ROOF | ROOF | 11387 | SIPLAST PARADIENE 20/30 FR | 2001-08-01 | ACOUSTICAL-METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5
142 | LaFollette | R18 | R18 | 00R | ROOF | ROOF | 5144 | UNKNOWN | 1997-08-01 | METAL | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -9
142 | LaFollette | R19 | R19 | 00R | ROOF | ROOF | 15850 | MANVILLE DYNAGLAS FR | 1992-08-01 | METAL | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14
142 | LaFollette | R20 | R20 | 00R | ROOF | ROOF | 25813 | GAF GAFGLAS MOD BIT | 1991-08-01 | METAL | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -15
142 | LaFollette | R21 | R21 | 00R | ROOF | ROOF | 13989 | UNKNOWN | 1992-08-01 | METAL | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14
142 | LaFollette | R22 | R22 | 00R | ROOF | ROOF | 24392 | UNKNOWN | 1992-08-01 | METAL | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14
142 | LaFollette | R23 | R23 | 00R | ROOF | ROOF | 1456 | MANVILLE DYNAKAP FR | 1992-08-01 | METAL | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14
142 | LaFollette | R24 | R24 | 00R | ROOF | ROOF | 982 | MANVILLE DYNAKAP FR | 1992-08-01 | 1.75" LT.WT. CONC OVER ME | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14
142 | LaFollette | R25 | R25 | 00R | ROOF | ROOF | 2173 | MANVILLE DYNAKAP FR | 1992-08-01 | 1" LT.WT. CONC. OVER META | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14
142 | LaFollette | R26 | R26 | 00R | ROOF | ROOF | 5570 | MANVILLE DYNAKAP FR | 1992-08-01 | METAL | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14
142 | LaFollette | R27 | R27 | 00R | ROOF | ROOF | 343 | MANVILLE DYNAKAP FR | 1992-08-01 | METAL | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14
142 | LaFollette | R28 | R28 | 00R | ROOF | ROOF | 2913 | MANVILLE DYNAKAP FR | 1992-08-01 | METAL | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14
142 | LaFollette | R29 | R29 | 00R | ROOF | ROOF | 373 | MANVILLE DYNAKAP FR | 1992-08-01 | METAL | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14
142 | LaFollette | R30 | R30 | 00R | ROOF | ROOF | 11239 | Tamko | 1995-08-01 | Metal | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -11
142 | LaFollette | R31 | R31 | 00R | ROOF | ROOF | 435 | Tamko | 1995-08-01 | Metal | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -11
142 | LaFollette | R32 | R32 | 00R | ROOF | ROOF | 6156 | SCHULLER 2FID MODIFIED | 1997-08-01 | METAL | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -9
142 | LaFollette | R33 | R33 | 00R | ROOF | ROOF | 8118 | SCHULLER 2FID MODIFIED | 1997-08-01 | METAL | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -9
142 | LaFollette | R34 | R34 | 00R | ROOF | ROOF | 4197 | UNKNOWN | 1992-08-01 | Metal | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14
142 | LaFollette | R35 | R35 | 00R | ROOF | ROOF | 824 | SARNIFIL | 1992-08-01 | Metal | 34 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -14
142 | LaFollette | R36 | R36 | 00R | ROOF | ROOF | 15874 | MANVILLE DYNAKAP FR | 1992-08-01 | METAL | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14
142 | LaFollette | R37 | R37 | 00R | ROOF | TEAM ROOM | 3500 | SIPLAST PARADIENE 20/30 FR | 2003-08-01 | METAL | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -3
142 | LaFollette | R38 | R38 | 00R | ROOF | MECHANICAL ROOM | 254 | SIPLAST PARADIENE 20/30 FR | 2003-08-01 | METAL | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -3
142 | LaFollette | R39 | R39 | 00R | ROOF | CONCESSION | 4800 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4
281252

## R143_R
Location Number | Location | Roof Identification Number | School Number | Level | Area Name | Roof Type | Area (Sq. Ft.) | Roof Type | Date Installed | Deck Information | Age (Years) | Drainage 0-Good Slope/No Ponding 3-Low Slope/Some Ponding 5-Poor Slope/Ponding | Blisters 0-No Blisters 3-Less Than 20 Percent 5-More Than 20 Percent | Linear Folds/Cracks 0-No Folds/Cracks 3-Less Than 20 Percent 5-More Than 20 Percent | Flashing Condition 0-Good 3-Some Splits/Cracks 5-Poor Splits/Cracks Common | Leakage Problems 0-No leaks 3-Minor Leaks 5-Major Leaks | Surface Wear 0-No Wear Noted 3-Average Wear Noted 5-Excessive Wear Noted | Deck 0-Concrete 3-Metal 5-Wood | Total Score Condition | Estimated Service Life | Estimated Remaining Life
143 | West | R01 | R01 | 00R | ROOF | ROOF | 2805 | MANVILLE DYNAKAP FR | 1992-08-01 | ACOUSTICAL-METAL | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14
143 | West | R02 | R02 | 00R | ROOF | ROOF | 17681 | MANVILLE DYNAKAP FR | 1992-08-01 | ACOUSTICAL-METAL | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -14
143 | West | R03 | R03 | 00R | ROOF | ROOF | 15985 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | UNKNOWN | 24 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -4
143 | West | R04 | R04 | 00R | ROOF | ROOF | 9737 | SIPLAST PARADIENE 20/30 FR | 1986-08-01 | METAL | 40 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -20
143 | West | R05 | R05 | 00R | ROOF | ROOF | 988 | SIPLAST PARADIENE 20/30 FR | 1986-08-01 | METAL | 40 | 5 | 0 | 0 | 5 | 3 | 3 | 3 | 39 | 20 | -20
143 | West | R06 | R06 | 00R | ROOF | ROOF | 2521 | SIPLAST PARADIENE 20/30 FR | 2000-08-01 | METAL | 26 | 5 | 5 | 0 | 0 | 0 | 3 | 0 | 18 | 15 | -11
143 | West | R07 | R07 | 00R | ROOF | ROOF | 5712 | SIPLAST PARADIENE 20/30 FR | 1986-08-01 | METAL | 40 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -20
143 | West | R08 | R08 | 00R | ROOF | ROOF | 706 | SIPLAST PARADIENE 20/30 FR | 1986-08-01 | METAL | 40 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -20
143 | West | R09 | R09 | 00R | ROOF | ROOF | 13362 | SIPLAST PARADIENE 20/30 FR | 1993-08-01 | METAL | 33 | 0 | 0 | 0 | 0 | 1 | 3 | 3 | 14 | 20 | -13
143 | West | R10 | R10 | 00R | ROOF | ROOF | 9759 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | UNKNOWN | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4
143 | West | R11 | R11 | 00R | ROOF | ROOF | 2159 | CLAY TILE | 1984-08-01 | METAL | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 33
143 | West | R12 | R12 | 00R | ROOF | ROOF | 1541 | SIPLAST PARADIENE 20/30 FR | 2000-08-01 | METAL | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | -11
143 | West | R13 | R13 | 00R | ROOF | ROOF | 8063 | CLAY TILE | 1984-08-01 | METAL | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 33
143 | West | R14 | R14 | 00R | ROOF | ROOF | 4837 | SIPLAST PARADIENE 20/30 FR | 2000-08-01 | METAL | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | -11
143 | West | R15 | R15 | 00R | ROOF | ROOF | 1517 | SIPLAST PARADIENE 20/30 FR | 2000-08-01 | METAL | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | -11
143 | West | R16 | R16 | 00R | ROOF | ROOF | 2219 | CLAY TILE | 1984-08-01 | METAL | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 33
143 | West | R17 | R17 | 00R | ROOF | ROOF | 6878 | SIPLAST PARADIENE 20/30 FR | 2003-08-01 | UNKNOWN | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -3
143 | West | R18 | R18 | 00R | ROOF | ROOF | 20592 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | UNKNOWN | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | -9
143 | West | R19 | R19 | 00R | ROOF | ROOF | 6804 | MANVILLE DYNAKAP FR | 1990-08-01 | METAL | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -16
143 | West | R20 | R20 | 00R | ROOF | ROOF | 1273 | BUR 4-PLY | 1965-08-01 | UNKNOWN | 61 | 5 | 0 | 0 | 5 | 3 | 3 | 5 | 43 | 20 | -41
143 | West | R21 | R21 | 00R | ROOF | ROOF | 597 | MANVILLE DYNAKAP FR | 1990-08-01 | METAL | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -16
135736

## R145_R
Location Number | Location | Roof Identification Number | School Number | Level | Area Name | Roof Type | Area (Sq. Ft.) | Roof Type | Date Installed | Deck Information | Age (Years) | Drainage 0-Good Slope/No Ponding 3-Low Slope/Some Ponding 5-Poor Slope/Ponding | Blisters 0-No Blisters 3-Less Than 20 Percent 5-More Than 20 Percent | Linear Folds/Cracks 0-No Folds/Cracks 3-Less Than 20 Percent 5-More Than 20 Percent | Flashing Condition 0-Good 3-Some Splits/Cracks 5-Poor Splits/Cracks Common | Leakage Problems 0-No leaks 3-Minor Leaks 5-Major Leaks | Surface Wear 0-No Wear Noted 3-Average Wear Noted 5-Excessive Wear Noted | Deck 0-Concrete 3-Metal 5-Wood | Total Score Condition | Estimated Service Life | Estimated Remaining Life
145 | Memorial | R01 | R01 | 00R | ROOF | GARAGE ROOF | 1450 | EPDM BALLAST | 1988-08-01 | METAL | 38 | 3 | 3 | 3 | 3 | 0 | 5 | 0 | 23 | 15 | -23
145 | Memorial | R02 | R02 | 00R | ROOF | RECEIVING ROOF | 419 | EPDM BALLAST | 1988-08-01 | METAL | 38 | 3 | 3 | 3 | 3 | 0 | 5 | 0 | 23 | 15 | -23
145 | Memorial | R03 | R03 | 00R | ROOF | BOILER ROOM ROOF | 2356 | BUR 4-PLY | 1965-08-01 | METAL | 61 | 0 | 3 | 3 | 3 | 0 | 5 | 0 | 17 | 20 | -41
145 | Memorial | R04 | R04 | 00R | ROOF | SPEC GYM ROOF | 19961 | TAMKO 704 | 1995-08-01 | METAL | 31 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 6 | 20 | -11
145 | Memorial | R05 | R05 | 00R | ROOF | STAGE ROOF | 2379 | MANVILLE DYNAKAP FR | 1987-08-01 | METAL | 39 | 3 | 3 | 0 | 0 | 0 | 3 | 0 | 12 | 20 | -19
145 | Memorial | R06 | R06 | 00R | ROOF | AUDITORIUM ROOF | 8145 | MANVILLE DYNAKAP FR | 1987-08-01 | METAL | 39 | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 9 | 20 | -19
145 | Memorial | R07 | R07 | 00R | ROOF | MUSIC WING ROOF | 6536 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4
145 | Memorial | R08 | R08 | 00R | ROOF | ROOF | 132 | SIPLAST PARADIENE 20/30 FR | 2002-08-01 | METAL | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -4
145 | Memorial | R09 | R09 | 00R | ROOF | COMMONS ROOF | 6604 | MANVILLE DYNAKAP FR | 1996-08-01 | METAL | 30 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -10
145 | Memorial | R10 | R10 | 00R | ROOF | PLANITARIUM | 1103 | MANVILLE DYNAKAP FR | 1996-08-01 | METAL | 30 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -10
145 | Memorial | R11 | R11 | 00R | ROOF | ROOF | 2646 | MANVILLE DYNAKAP FR | 1996-08-01 | METAL | 30 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -10
145 | Memorial | R12 | R12 | 00R | ROOF | ROOF | 1772 | MANVILLE DYNAKAP FR | 1996-08-01 | METAL | 30 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -10
145 | Memorial | R13 | R13 | 00R | ROOF | ROOF | 680 | MANVILLE DYNAKAP FR | 1996-08-01 | METAL | 30 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -10
145 | Memorial | R14 | R14 | 00R | ROOF | ROOF | 18026 | MANVILLE DYNAKAP FR | 1987-08-01 | METAL | 39 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -19
145 | Memorial | R15 | R15 | 00R | ROOF | ROOF | 11429 | MANVILLE DYNAKAP FR | 1987-08-01 | METAL | 39 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -19
145 | Memorial | R16 | R16 | 00R | ROOF | ROOF | 17660 | MANVILLE DYNAKAP FR | 1988-08-01 | METAL | 38 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -18
145 | Memorial | R17 | R17 | 00R | ROOF | ROOF | 3663 | MANVILLE DYNAKAP FR | 1988-08-01 | METAL | 38 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -18
145 | Memorial | R18 | R18 | 00R | ROOF | ROOF | 2726 | MANVILLE DYNAKAP FR | 1988-08-01 | METAL | 38 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -18
145 | Memorial | R19 | R19 | 00R | ROOF | ROOF | 9456 | SIPLAST PARADIENE 20/30 FR | 1996-08-01 | METAL | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -10
145 | Memorial | R20 | R20 | 00R | ROOF | ROOF | 12811 | MANVILLE DYNAKAP FR | 1996-08-01 | METAL | 30 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -10
145 | Memorial | R21 | R21 | 00R | ROOF | ROOF | 16007 | MODIFIED BIT. | 1995-08-01 | METAL | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -11
145 | Memorial | R22 | R22 | 00R | ROOF | ROOF | 8393 | SIPLAST PARADIENE 20/30 FR | 1999-08-01 | METAL | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -7
145 | Memorial | R23 | R23 | 00R | ROOF | FH ENTRANCE | 500 | MANVILLE DYNAKAP FR | 1992-08-01 | METAL | 34 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -14
145 | Memorial | R24 | R24 | 00R | ROOF | FH | 28009 | MANVILLE DYNAKAP FR | 1992-08-01 | METAL | 34 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -14
145 | Memorial | R25 | R25 | 00R | ROOF | FH MECHANICAL | 3124 | MANVILLE DYNAKAP FR | 1992-08-01 | METAL | 34 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -14
145 | Memorial | R26 | R26 | 00R | ROOF | FH LOCKER RM | 5061 | MANVILLE DYNAKAP FR | 1992-08-01 | METAL | 34 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -14
145 | Memorial | R27 | R27 | 00R | ROOF | SPORTS TRAINING ROOM | 1273 | SIPLAST PARADIENE 20/30 FR | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5
145 | Memorial | R28 | R28 | 00R | ROOF | ROOF | 7070 | SIPLAST PARADIENE 20/30 FR | 1996-08-01 | METAL | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -10
145 | Memorial | R29 | R29 | 00R | ROOF | ROOF | 8312 | SIPLAST PARADIENE 20/30 FR | 1996-08-01 | METAL | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -10
145 | Memorial | R30 | R30 | 00R | ROOF | ROOF | 4476 | SIPLAST PARADIENE 20/30 FR | 1999-08-01 | METAL | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -7
145 | Memorial | R31 | R31 | 00R | ROOF | ROOF | 7988 | SIPLAST PARADIENE 20/30 FR | 1999-08-01 | METAL | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -7
145 | Memorial | R32 | R32 | 00R | ROOF | ROOF | 11555 | SIPLAST PARADIENE 20/30 FR | 1996-08-01 | METAL | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -10
145 | Memorial | R33 | R33 | 00R | ROOF | ROOF | 1811 | MANVILLE DYNAKAP FR | 1987-08-01 | METAL | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -19
145 | Memorial | R34 | R34 | 00R | ROOF | ROOF | 457 | SIPLAST PARADIENE 20/30 FR | 1987-08-01 | METAL | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -19
145 | Memorial | R35 | R35 | 00R | ROOF | NEIGHBORHOOD ROOM | 1327 | SIPLAST PARADIENE 20/30 FR | 2001-08-01 | METAL | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -5
145 | Memorial | R36 | R36 | 00R | ROOF | ROOF | 280 | SIPLAST PARADIENE 20/30 FR | 1996-08-01 | METAL | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -10
145 | Memorial | R37 | R37 | 00R | ROOF | ROOF | 17524 | MANVILLE DYNAKAP FR | 1987-08-01 | METAL | 39 | 0 | 3 | 3 | 0 | 0 | 3 | 0 | 12 | 20 | -19
145 | Memorial | R38 | R38 | 00R | ROOF | ROOF | 11048 | MANVILLE DYNAKAP FR | 1988-08-01 | METAL | 38 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -18
145 | Memorial | R39 | R39 | 00R | ROOF | MANSFIELD | 3787 | SIPLAST PARADIENE 20/30 FR | 1999-08-01 | METAL | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -7
145 | Memorial | R40 | R40 | 00R | ROOF | MANSFIELD | 5040 | SIPLAST PARADIENE 20/30 FR | 1999-08-01 | METAL | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -7
145 | Memorial | R41 | R41 | 00R | ROOF | MANSFIELD | 2568 | SIPLAST PARADIENE 20/30 FR | 1999-08-01 | METAL | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -7
145 | Memorial | R42 | R42 | 00R | ROOF | CONCESSION | 800 | SIPLAST PARADIENE 20/30 FR | 1998-08-01 | METAL | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -8
145 | Memorial | R43 | R43 | 00R | ROOF | MANSFIELD | 3804 | SIPLAST PARADIENE 20/30 FR | 1999-08-01 | METAL | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -7

## x001_r
Location Number | Location | Roof Identification Number | School Number | Level | Area Name | Roof Type | Area (Sq. Ft.) | Roof Type | Date Installed | Deck Information | Age (Years) | Drainage 0-Good Slope/No Ponding 3-Low Slope/Some Ponding 5-Poor Slope/Ponding | Blisters 0-No Blisters 3-Less Than 20 Percent 5-More Than 20 Percent | Linear Folds/Cracks 0-No Folds/Cracks 3-Less Than 20 Percent 5-More Than 20 Percent | Flashing Condition 0-Good 3-Some Splits/Cracks 5-Poor Splits/Cracks Common | Leakage Problems 0-No leaks 3-Minor Leaks 5-Major Leaks | Surface Wear 0-No Wear Noted 3-Average Wear Noted 5-Excessive Wear Noted | Deck 0-Concrete 3-Metal 5-Wood | Total Score Condition | Estimated Service Life | Estimated Remaining Life
001 | Allis | C01 | C01 | 00R | CANOPY | ROOF | 97 | SIPLAST PARADIENE 20/30 FR | 2004-08-04 | UNKNOWN | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | -7
001 | Allis | C02 | C02 | 00R | CANOPY | ROOF | 97 | SIPLAST PARADIENE 20/30 FR | 2004-08-04 | UNKNOWN | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | -7
001 | Allis | C03 | C03 | 00R | CANOPY | ROOF | 64 | SIPLAST PARADIENE 20/30 FR | 2004-08-04 | UNKNOWN | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | -7
001 | Allis | C04 | C04 | 00R | CANOPY | ROOF | 142 | SIPLAST PARADIENE 20/30 FR | 2004-08-04 | UNKNOWN | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | -7
001 | Allis | R01 | R01 | 00R | LOCKER | ROOF | 2551 | SIPLAST PARADIENE 20/30 FR | 2004-08-04 | UNKNOWN | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | -7
001 | Allis | R02 | R02 | 00R | GYM | ROOF | 6031 | SIPLAST PARADIENE 20/30 FR | 1985-08-01 | UNKNOWN | 41 | 3 | 1 | 0 | 0 | 0 | 3 | 0 | 10 | 20 | -21
001 | Allis | R03 | R03 | 00R | TRACTOR | ROOF | 309 | SIPLAST PARADIENE 20/30 FR | 2004-08-04 | UNKNOWN | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | -2
001 | Allis | R04 | R04 | 00R | ROOF | ROOF | 2899 | SIPLAST PARADIENE 20/30 FR | 1985-08-01 | UNKNOWN | 41 | 3 | 0 | 0 | 1 | 3 | 3 | 5 | 35 | 20 | -21
001 | Allis | R05 | R05 | 00R | ROOF | ROOF | 2010 | SIPLAST PARADIENE 20/30 FR | 1985-08-01 | UNKNOWN | 41 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 20 | -21
001 | Allis | R06 | R06 | 00R | ROOF | ROOF | 4510 | SIPLAST PARADIENE 20/30 FR | 1985-08-01 | UNKNOWN | 41 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -21
001 | Allis | R07 | R07 | 00R | ROOF | ROOF | 5973 | SIPLAST PARADIENE 20/30 FR | 1985-08-01 | UNKNOWN | 41 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -21
001 | Allis | R08 | R08 | 00R | ROOF | ROOF | 3602 | SIPLAST PARADIENE 20/30 FR | 1985-08-01 | UNKNOWN | 41 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | 20 | -21
001 | Allis | R09 | R09 | 00R | ROOF | ROOF | 7390 | SIPLAST PARADIENE 20/30 FR | 1985-08-01 | UNKNOWN | 41 | 3 | 3 | 0 | 0 | 0 | 3 | 0 | 12 | 20 | -21
001 | Allis | R10 | R10 | 00R | ROOF | ROOF | 954 | SIPLAST PARADIENE 20/30 FR | 2004-08-04 | UNKNOWN | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | -7
001 | Allis | R11 | R11 | 00R | ENTRANCE | ROOF | 335 | COPPER | 1965-08-01 | UNKNOWN | 61 | 0 | 0 | 0 | 5 | 3 | 3 | 5 | 33 | 15 | -46
36964
73928